## Slide 1
KNOWLEDGE BASE · 知识库
Data Center Fundamentals
数据中心基础知识
What a data center is, how it is classified, its spaces, major and secondary equipment, supporting systems and the project lifecycle — the common basis for project technical assessment.
什么是数据中心、如何分类、功能区、主要与次要设备、支持系统及项目全生命周期——项目技术评估的共同知识基础。
Project Technical Assessment · 项目技术评估 | Rev. 3 | October 2026

## Slide 2: What this deck covers
本演示文稿内容
01
What is a Data Center?
什么是数据中心？
Definition, how it works, key metrics
定义、工作原理、关键指标
02
Classification & Tiers
分类与等级
Types, sizes, Tier I–IV, standards
类型、规模、Tier I–IV、标准
03
Spaces & Layout
功能区与布局
White, grey, support & site areas
白区、灰区、支持区与场地
04
Electrical Systems
电气系统
Utility to rack: MV, UPS, generators
从市电到机柜：中压、UPS、发电机
05
Cooling Systems
制冷系统
Chillers, CRAH, liquid cooling, PUE
冷机、精密空调、液冷、PUE
06
IT & Network
IT与网络
Racks, cabling, connectivity
机柜、布线、网络连接
07
Safety, Security & Monitoring
安全、安防与监控
Fire, physical security, BMS/DCIM
消防、物理安防、BMS/DCIM
08
Supporting Systems & Lifecycle
支持系统与生命周期
Civil, cost, schedule, commissioning
土建、投资、进度、调试
09
Project Development (2026)
项目开发（2026）
PLN, platforms, cooling, BESS, cost, returns, permits
PLN、平台、制冷、储能、投资、回报、许可

## Slide 3: What is a Data Center?
01
什么是数据中心？
A purpose-built facility that keeps computing, storage and network equipment running 24/7.
为计算、存储和网络设备提供7×24不间断运行环境的专用设施。

## Slide 4: A building engineered around uninterrupted IT
围绕“不间断IT”而设计的建筑
A data center houses IT equipment and provides everything it needs to run continuously: conditioned power, cooling, connectivity, security and 24/7 operations.
数据中心容纳IT设备，并提供其持续运行所需的一切：稳定电力、制冷、网络连接、安全保障及7×24运维。
IT load (MW) — the electrical power consumed by servers — is the basic unit of size.
IT负载（MW）——服务器消耗的电功率——是衡量规模的基本单位。
Almost every watt delivered to IT becomes heat that must be removed.
输送给IT的几乎每一瓦电力都会变成必须排除的热量。
Availability is designed in through redundancy (N+1, 2N) and maintainability.
可用性通过冗余（N+1、2N）及可维护性设计来实现。
Data centres used ≈ 415 TWh in 2024 (≈ 1.5% of world electricity), projected to roughly double by 2030 (IEA).
2024年数据中心用电约415 TWh（约占全球1.5%），预计到2030年约翻一番（IEA）。
IT equipment
IT设备
Power
电力
Cooling
制冷
Connectivity
网络连接
Security & fire
安防与消防
Operations 24/7
7×24运维
Building & site
建筑与场地

## Slide 5: How a data center works: power in, heat out, data through
工作原理：电力输入、热量排出、数据流通
Utility grid
市电电网
Power chain
供电链
IT racks
IT机柜
Heat
热量
Cooling chain
制冷链
Atmosphere
大气
Transformers, switchgear, UPS + batteries and generators condition and back up power.
变压器、开关柜、UPS+电池及发电机负责电力调理与备用。
Servers, storage and switches turn ≈ 100% of input power into heat.
服务器、存储与交换机几乎将100%输入功率转化为热量。
CRAH / CDU → chillers → cooling towers or dry coolers reject heat outside.
精密空调/CDU→冷机→冷却塔或干冷器将热量排至室外。
DATA PATH · 数据路径
Carriers & internet
运营商与互联网
Diverse fibre entries
分离光纤入口
Meet-Me Room
运营商交汇间
Core / spine-leaf
核心/叶脊网络
Servers & storage
服务器与存储
Redundant paths everywhere: two power paths, N+1 cooling, two fibre routes.
处处冗余：双供电路径、N+1制冷、双光纤路由。

## Slide 6: Five numbers that describe any data center
描述任何数据中心的五个关键数字
MW
IT load
IT负载
Design power for IT equipment — sets the size of everything else.
IT设备设计功率——决定其他一切的规模。
kW/rack
Rack density
机柜功率密度
5–15 kW enterprise / cloud; 40–140 kW AI GPU racks.
企业/云5–15 kW；AI GPU机柜40–140 kW。
PUE
Power Usage Effectiveness
电能利用效率
Total ÷ IT energy. Global average ≈ 1.5; best ≈ 1.1.
总能耗÷IT能耗。全球平均约1.5；最佳约1.1。
WUE
Water Usage Effectiveness
水利用效率
Litres of water per kWh of IT energy (0 – 2+).
每kWh IT能耗的用水量（0–2+升）。
99.982%
Availability (Tier III)
可用性（Tier III）
≈ 1.6 h/year of downtime — designed via redundancy.
每年约1.6小时停机——通过冗余设计实现。

## Slide 7: Classification & Tier Standards
02
分类与等级标准
By business model, by size and by resilience (Tier / Rated / Class).
按商业模式、按规模、按韧性（Tier / Rated / Class）分类。

## Slide 8: Eight common types of data center
八种常见数据中心类型
Enterprise (Owner-operated)
企业自建（自用）
Built and operated by one organisation for its own IT.
由单一机构为自身IT建设并运营。
200 kW – 10 MW | 5–12 kW/rack
Retail Colocation
零售型托管
Operator leases racks, cages and suites to many tenants; carrier-neutral interconnection is a key value.
运营商向众多租户出租机柜、笼位和包间；运营商中立的互联是核心价值。
2 MW – 30 MW | 6–15 kW/rack
Wholesale / Build-to-Suit
批发型 / 定制建设
Whole data halls or buildings leased to a single large tenant (often a cloud provider) on long terms.
整个机房或整栋楼长期租给单一大租户（通常为云服务商）。
10 MW – 100 MW | 10–25 kW/rack
Hyperscale / Cloud
超大规模 / 云
Campus-scale facilities owned or leased by cloud and internet giants, highly standardised and efficient.
云与互联网巨头自有或租赁的园区级设施，高度标准化、高能效。
30 MW – 500 MW | 12–30 kW/rack
AI Factory / HPC
AI算力中心 / 高性能计算
GPU clusters for AI training and inference; 40–140 kW per rack, liquid cooling, very large single-site power.
用于AI训练和推理的GPU集群；单柜40–140 kW，液冷，单站点用电极大。
5 MW – 1 GW | 40–140 kW/rack
Edge / Micro Data Center
边缘 / 微型数据中心
Sites close to users or devices for low latency (5G, CDN, IoT, AI inference) — from micro sites to regional edge campuses; often prefabricated.
靠近用户或设备以降低时延的站点（5G、CDN、物联网、AI推理）——从微型站点到区域边缘园区；常为预制式。
50 kW – 30 MW | 5–20 kW/rack
Government / Sovereign
政府 / 主权数据中心
National or regional government facilities with data-sovereignty and high-security requirements.
具有数据主权及高安全要求的国家或地方政府设施。
1 MW – 50 MW | 6–20 kW/rack
Modular / Prefabricated
模块化 / 预制式
Factory-built power, cooling and IT modules assembled on site — faster delivery and phased growth.
在工厂预制电力、制冷与IT模块并在现场拼装——交付更快、可分期扩展。
200 kW – 20 MW | 8–40 kW/rack

## Slide 9: Size classes by IT load
按IT负载划分的规模等级
< 0.5 MW
Micro / Edge
微型 / 边缘
≤ 100 racks
≤ 100 个机柜
0.5 – 2 MW
Small
小型
100 – 400 racks
100 – 400 个机柜
2 – 10 MW
Medium
中型
400 – 1,500 racks
400 – 1,500 个机柜
10 – 30 MW
Large
大型
1,500 – 4,000 racks
1,500 – 4,000 个机柜
30 – 100 MW
Hyperscale building
超大规模单体
4,000 – 10,000 racks
4,000 – 10,000 个机柜
> 100 MW
Hyperscale / AI campus
超大规模 / AI园区
> 10,000 racks
> 10,000 个机柜
Rack counts assume 5–10 kW per rack; AI racks at 100+ kW pack the same MW into far fewer racks and less floor area.
机柜数量按每柜5–10 kW估算；100 kW以上的AI机柜可用更少的机柜和更小的面积容纳同等MW。

## Slide 10: Uptime Institute Tiers I–IV: resilience by design
Uptime Tier I–IV：通过设计实现韧性
TIER I
Basic Capacity
基本容量
99.671%
≈ 28.8 h downtime / yr 年停机
Redundancy N · paths 1
冗余 N · 路径 1
Single path, no redundant components. Any maintenance or failure causes an outage.
单一路径，无冗余组件。任何维护或故障都会导致停机。
TIER II
Redundant Capacity Components
冗余容量组件
99.741%
≈ 22.7 h downtime / yr 年停机
Redundancy N+1 · paths 1
冗余 N+1 · 路径 1
Redundant UPS, generators and chillers (N+1) on a single distribution path; path maintenance still needs shutdown.
UPS、发电机、冷机冗余（N+1），但为单一配电路径；路径维护仍需停机。
TIER III
Concurrently Maintainable
可同时维护
99.982%
≈ 1.6 h downtime / yr 年停机
Redundancy N+1 · paths 1 active + 1 alternate
冗余 N+1 · 路径 1 主用 + 1 备用
Every component and distribution path can be removed for planned maintenance without impacting IT. Dual-corded IT; ≥ 12 h on-site fuel.
任一组件和配电路径均可在计划维护时退出而不影响IT。IT双电源；现场燃油≥12 h。
TIER IV
Fault Tolerant
容错
99.995%
≈ 26.3 min downtime / yr 年停机
Redundancy 2N / 2(N+1) · paths 2 active
冗余 2N / 2(N+1) · 路径 2 主用
Any single unplanned failure is tolerated automatically. Two simultaneously active paths, compartmentalisation and continuous cooling.
可自动承受任何单一非计划故障。两条同时运行的路径、物理分区隔离及连续制冷。
Availability figures are the commonly cited Uptime benchmarks; real availability depends equally on operations.
可用性数值为常用的Uptime参考值；实际可用性同样取决于运维水平。

## Slide 11: Redundancy explained: N, N+1, 2N, 2(N+1)
冗余释义：N、N+1、2N、2(N+1)
N
Exactly the capacity needed. One failure = outage.
恰好满足需求的容量。任一故障即停机。
N+1
One spare unit. Survives one component failure or maintenance.
一台备用。可承受一个组件故障或维护。
2N
A
B
Two complete, independent systems (A + B). Survives loss of a whole path.
两套完整独立系统（A+B）。可承受整路失效。
2(N+1)
A
B
Two independent systems, each with its own spare. Highest resilience.
两套独立系统，各自带备用。韧性最高。

## Slide 12: One concept, many standards: classification cross-reference
同一概念、多套标准：分级对照
Uptime Institute | TIA-942-C | EN 50600 / ISO 22237 | GB 50174 (China) | SNI 8799 (Indonesia) | BICSI 002 | Design intent / 设计意图
Tier I | Rated-1 | Class 1 | C 级 | Strata I | Class F1 | Basic, single path 基本，单路径
Tier II | Rated-2 | Class 2 | B 级 (partial) | Strata II | Class F2 | Redundant components 组件冗余
Tier III | Rated-3 | Class 3 | B 级 / A 级 (partial) | Strata III | Class F3 | Concurrently maintainable 可同时维护
Tier IV | Rated-4 | Class 4 | A 级 | Strata IV | Class F4 | Fault tolerant 容错
Mappings are approximate — each scheme has its own detailed criteria and certification process.
对照为近似关系——各体系有各自的详细准则和认证流程。
Uptime certifies Design, Constructed Facility and Operational Sustainability separately.
Uptime分别认证设计、建成设施和运营可持续性。
Chinese GB 50174 Class A broadly aligns with fault-tolerant design; SNI 8799 Strata IV requires 2N with automatic failover.
中国GB 50174 A级大致对应容错设计；SNI 8799 Strata IV要求2N及自动切换。

## Slide 13: Key codes & standards by discipline
各专业主要规范与标准
Design & topology
设计与拓扑
Uptime Tier Standard · TIA-942-C · EN 50600 / ISO 22237 · BICSI 002 · GB 50174 · SNI 8799
Electrical
电气
IEC 62271 · IEC 61439 · IEC 60076 · IEC 62040 (UPS) · ISO 8528 (gensets) · IEC 62305 · NFPA 70/110 · PUIL
Mechanical
暖通
ASHRAE TC 9.9 Thermal Guidelines · ASHRAE 90.4 · AHRI 550/590 · ASHRAE 127 · GB 50019
Fire & life safety
消防与生命安全
NFPA 75 / 76 · NFPA 2001 · NFPA 72 / 13 · NFPA 855 (Li-ion) · GB 50370 · GB 50116 · SNI 03-3985
IT & cabling
IT与布线
TIA-568 · TIA-569 · TIA-606 · TIA-607 · ISO/IEC 11801 · GB 50311
Energy & sustainability
能效与可持续
ISO/IEC 30134 (PUE, WUE, CUE) · ISO 50001 · GB 40879 (PUE grades) · EU EED reporting · SS 564

## Slide 14: Spaces & Layout
03
功能区与布局
White space hosts IT; grey space hosts the plant that keeps it alive.
白区承载IT；灰区承载维持其运行的设备。

## Slide 15: Four zones of a data center facility
数据中心设施的四大区域
White Space
白区（IT空间）
Where IT equipment lives. Clean, secure, precisely cooled.
IT设备所在区域。洁净、安全、精密制冷。
Data hall / computer room
数据机房 / 主机房
Entrance room / Meet-Me Room (MMR)
进线间 / 运营商交汇间
Main Distribution Area (MDA)
主配线区（MDA）
Horizontal / Zone Distribution Area (HDA/ZDA)
水平 / 区域配线区（HDA/ZDA）
Equipment Distribution Area (EDA) — rack rows
设备配线区（EDA）——机柜列
Customer cages & suites
客户笼位及包间
Grey Space
灰区（基础设施空间）
Plant rooms housing power and cooling infrastructure that support the white space.
容纳支持白区的电力与制冷基础设施的设备间。
MV switchgear room / utility intake
中压开关室 / 市电进线
Transformer room / yard
变压器室 / 变压器场
LV switchboard room
低压配电室
UPS room
UPS室
Battery room
电池室
Generator hall / yard & fuel farm
发电机房 / 发电机场地及油库
Support Space
支持区（辅助空间）
Spaces for people, logistics and operations.
供人员、物流及运营使用的空间。
Network/Security Operations Center (NOC/SOC)
网络/安全运营中心（NOC/SOC）
Loading dock & freight lift
装卸平台及货梯
Staging, build & burn-in room
设备预置、组装及老化测试间
Storage & spare parts
库房及备品备件
Security control & mantrap lobby
安保控制室及防尾随门厅
Offices, customer lounge, meeting rooms
办公室、客户休息区、会议室
Site & External Works
场地及室外工程
Everything outside the building envelope.
建筑围护结构之外的一切。
Perimeter fence, gatehouse & vehicle barriers
周界围栏、门卫室及车辆拦阻
Utility substation (HV/MV)
变电站（高压/中压）
Diverse fibre duct banks & manholes
分离光缆管群及人孔
Water storage & treatment
储水及水处理
Roads, parking & landscaping
道路、停车及景观
Future expansion land
未来扩建用地

## Slide 16: Typical site plan of a Tier III campus
典型Tier III园区总平面
Data halls (white space)
数据机房（白区）
UPS & LV rooms
UPS及低压室
Chiller plant
冷站
Support: NOC, loading dock, staging, offices
支持区：NOC、装卸平台、预置区、办公
Generator yard
发电机场地
Fuel farm
油库
Cooling towers
冷却塔
MV / HV substation
中/高压变电站
Parking
停车场
Gatehouse
门卫
Future expansion
预留扩建用地
Ring road / 环形道路
Fibre route A / 光纤路由A
Route B / 路由B
Security fence + PIDS / 安全围栏+入侵探测
Separate the generator exhaust from cooling and fresh-air intakes (prevailing wind).
发电机排气与冷却及新风进风口分开（考虑主导风向）。
Two diverse utility feeds and two fibre entry routes ≥ 20 m apart.
两路分离市电进线及两条相距≥20 m的光纤入口路由。
Plant yards sized for crane access and future equipment replacement.
设备场地满足吊车通道及未来设备更换。
Reserve land for phases; pre-build shared infrastructure.
为后续分期预留用地；共享基础设施预先建设。
Stand-off distance and anti-ram barriers at the perimeter.
周界设安全距离及防冲撞设施。

## Slide 17: Inside the data hall: hot aisle / cold aisle
数据机房内部：热通道 / 冷通道
Fan wall / CRAH 风墙/精密空调
COLD AISLE 22–27 °C 冷通道
HOT AISLE 35–45 °C (contained) 热通道（封闭）
COLD AISLE 22–27 °C 冷通道
Overhead busway & fibre raceway above racks · 机柜上方：插接母线与光纤槽道
Racks face each other: fronts draw cold air, backs exhaust hot air.
机柜面对面布置：正面吸入冷风，背面排出热风。
Containment stops mixing — enabling warmer supply air and lower fan energy.
通道封闭防止混风——可提高送风温度、降低风机能耗。
Air cooling is practical to ≈ 25 kW/rack; above that use in-row, rear-door or liquid cooling.
风冷实际上限约25 kW/柜；更高密度采用列间、背板或液冷。
Typical pitch 2.4 m per row pair; ≈ 2.5–3.5 m² of white space per rack incl. circulation.
每对机柜列间距约2.4 m；含通道每柜约2.5–3.5 m²白区面积。

## Slide 18: Telecom spaces & cabling topology (TIA-942)
通信空间及布线拓扑（TIA-942）
Carrier A
运营商A
Carrier B
运营商B
Entrance Room / MMR 1
进线间 / MMR 1
Entrance Room / MMR 2
进线间 / MMR 2
Main Distribution Area
主配线区（MDA）
HDA (row)
水平配线区
HDA (row)
水平配线区
HDA (row)
水平配线区
→ EDA: equipment racks (servers, storage) 设备配线区：设备机柜
Entrance Room / MMR: carriers terminate here; carrier-neutral sites offer many carriers and cross-connects.
进线间/MMR：运营商在此成端；运营商中立的场地可提供多家运营商及交叉连接。
MDA: core routers & switches and the main cross-connect for the whole facility.
MDA：核心路由器、交换机及全设施主交叉连接。
HDA / ZDA: row- or zone-level distribution to the Equipment Distribution Areas (racks).
HDA/ZDA：列级或区域级配线，连接至设备配线区（机柜）。
Rated-3/4: two entrance rooms, diverse pathways and redundant backbone cabling.
Rated-3/4：两个进线间、分离路由及冗余主干布线。

## Slide 19: Space planning rules of thumb
空间规划经验值
2.5–3.5 m²
White space per rack (incl. aisles)
每柜白区面积（含通道）
4.5–6 m
Clear height in data halls
机房净高
15–25
kN/m² floor load (AI up to 25)
kN/m²楼面荷载（AI可达25）
500–1,500
m² gross floor area per MW IT
每MW IT对应总建筑面积m²
Ratios vary with density, Tier and battery type: Tier IV roughly doubles electrical rooms; Li-ion batteries need ≈ 1/3 of VRLA space.
比例随密度、等级及电池类型变化：Tier IV电气房间约翻倍；锂电所需空间约为铅酸的1/3。
Chart: Typical gross-area mix (Tier III, air-cooled) 典型面积构成
| White space 白区 | Electrical rooms 电气 | Mechanical 暖通 | Support 支持区 | Circulation & walls 交通
Space mix | 35 | 25 | 15 | 10 | 15

## Slide 20: Electrical Power Systems
04
电气供配电系统
From the utility substation to the server power supply — with no single point of failure.
从变电站到服务器电源——无单点故障。

## Slide 21: The critical power chain (2N “A/B” example)
关键供电链（2N“A/B”示例）
Utility feed
市电进线
Utility feed
市电进线
MV switchgear
中压开关柜
MV switchgear
中压开关柜
Transformer
变压器
Transformer
变压器
LV switchboard
低压配电柜
LV switchboard
低压配电柜
UPS + battery
UPS+电池
UPS + battery
UPS+电池
PDU / busway
PDU / 母线
PDU / busway
PDU / 母线
Rack PDU
机架PDU
Rack PDU
机架PDU
PATH A
PATH B
Generators + ATS
发电机+ATS
Dual-corded server
双电源服务器
20 kV / 150 kV utility (PLN) — two feeds recommended for Tier III/IV
20 kV / 150 kV市电（PLN）——Tier III/IV建议双路
2,500 kVA dry-type, Dyn11, 20/0.4 kV
2,500 kVA干式变压器，Dyn11，20/0.4 kV
UPS bridges 10–60 s until generators carry the load; 5–10 min batteries
UPS在发电机接带前桥接10–60 s；电池5–10 min
Every component can be maintained (Tier III) or fail (Tier IV) without dropping IT
任一组件可维护（Tier III）或故障（Tier IV）而不影响IT

## Slide 22: Major electrical equipment (1/2): MV, transformers, generators
主要电气设备（1/2）：中压、变压器、发电机
Medium Voltage Switchgear
中压开关柜
Metal-clad, withdrawable VCB, 12 / 24 / 40.5 kV, 630–2500 A busbar, 25–31.5 kA. AIS or GIS where space is limited.
金属铠装、手车式真空断路器，12 / 24 / 40.5 kV，母线630–2500 A，25–31.5 kA；空间受限时采用GIS。
Switchgear shall be metal-enclosed, LSC2B-PM, with internal arc classification IAC AFLR and withdrawable vacuum circuit breakers.
开关柜应为金属封闭型，运行连续性等级LSC2B-PM，内部燃弧等级IAC AFLR，配手车式真空断路器。
Double incoming feeders with bus-section (bus-coupler) breaker and automatic changeover shall be provided for Tier III/IV designs.
Tier III/IV设计应设双路进线及母联断路器，并具备自动切换功能。
MV/LV Power Transformer (Cast-Resin Dry-Type)
中压/低压电力变压器（环氧树脂浇注干式）
1,600 – 3,150 kVA per unit (2,500 kVA most common); one transformer per “block” of ~1.5–2 MW facility load.
单台1,600–3,150 kVA（以2,500 kVA最常见）；每台对应约1.5–2 MW设施负荷的一个“供电模块”。
Indoor cast-resin, class F insulation (temperature rise limited to class B or 100 K) with E2-C2-F1 climatic/environmental/fire class.
户内环氧树脂浇注干式，F级绝缘（温升按B级或100 K考核），环境/气候/燃烧等级E2-C2-F1。
Losses shall comply with EU Ecodesign Tier 2 / GB 20052 energy efficiency grade 2 or better.
损耗应满足欧盟Ecodesign Tier 2或GB 20052二级能效及以上。
Diesel Generator Set
柴油发电机组
1,500 – 3,250 kVA per unit (2.0–2.5 MWe typical) at 400 V LV or 11/20 kV MV, containerised or in a generator hall.
单台1,500–3,250 kVA（典型2.0–2.5 MWe），低压400 V或中压11/20 kV，集装箱式或机房式。
Rating shall be Continuous (COP) or Data Center Continuous (DCC) with no annual run-hour limit at site conditions to satisfy Tier III/IV.
为满足Tier III/IV，额定功率应为持续功率（COP）或数据中心持续功率（DCC），在现场条件下无年运行小时限制。
Start, synchronise and accept load within 10–15 s; single-step load acceptance per ISO 8528-5 performance class G3.
10–15 s内完成启动、同步并接带负荷；突加负荷性能满足ISO 8528-5 G3级。

## Slide 23: Major electrical equipment (2/2): UPS & batteries
主要电气设备（2/2）：UPS与电池
Static UPS — double conversion
静态UPS——双变换
Modular or monolithic double-conversion, 500–1,600 kW per system (modules 50–250 kW), 400/415 V, efficiency 96–97% (99% eco).
模块化或塔式双变换，单系统500–1,600 kW（模块50–250 kW），400/415 V，效率96–97%（ECO模式99%）。
Double conversion isolates IT from every grid disturbance (VFI-SS-111).
双变换将IT与电网扰动完全隔离（VFI-SS-111）。
Eco-mode raises efficiency to ≈ 99% but with less isolation.
ECO模式效率约99%，但隔离程度降低。
Rotary / DRUPS (flywheel + diesel) is an alternative with no batteries.
旋转式/柴油动态UPS（飞轮+柴油机）是无电池的替代方案。
Modular frames let capacity grow in 50–250 kW steps.
模块化机架可按50–250 kW逐步扩容。
Battery comparison 电池对比 | VRLA lead-acid 阀控铅酸 | Li-ion (LFP) 锂电（磷酸铁锂）
Design life 设计寿命 | 5 – 10 yrs | 12 – 15 yrs
Footprint & weight 占地与重量 | 100% | ≈ 30–40%
Room temperature 室温要求 | 20–25 °C | 18–30 °C
Initial cost 初投资 | Lower 较低 | Higher 较高
Monitoring 监测 | Per-block (optional) 按单体（可选） | Built-in BMS 内置BMS
Fire risk 火灾风险 | Hydrogen venting 需排氢 | Thermal runaway — NFPA 855, UL 9540A 热失控——NFPA 855、UL 9540A

## Slide 24: Getting power to the rack — and sizing the plant
电力送达机柜——以及设备容量估算
Floor PDU / RPP
落地PDU / RPP
150–400 kVA cabinets with branch breakers; under-floor or overhead cables. Best ≤ 10 kW/rack.
150–400 kVA配电柜带分支断路器；地板下或上走线电缆。适合≤10 kW/柜。
Overhead busway
上走线插接母线
400–800 A plug-in busbar per row, A + B; tap-off boxes per rack. Flexible for growth.
每列400–800 A插接母线，A+B双路；每柜插接箱。便于扩展。
Rack PDU
机架PDU
1-ph 32 A (7.4 kW) · 3-ph 32 A (22 kW) · 3-ph 63 A (43 kW); two per rack (A/B).
单相32 A（7.4 kW）·三相32 A（22 kW）·三相63 A（43 kW）；每柜两条（A/B）。
Quick sizing rules
快速估算规则
Facility demand ≈ IT × design-day PUE (+ battery recharge)
设施需量 ≈ IT × 设计日PUE（+电池充电）
Utility MVA ≈ facility kW ÷ 0.95
市电MVA ≈ 设施kW ÷ 0.95
Transformers: one 2,500 kVA per ≈ 2 MW facility load
变压器：每约2 MW设施负荷配一台2,500 kVA
Generators: (facility kW ÷ unit kW) + redundancy
发电机：（设施kW÷单机kW）+冗余
Diesel ≈ 0.27 L per kWh — 10 MW for 24 h ≈ 65 m³
柴油约0.27 L/kWh——10 MW运行24 h约65 m³
Battery kWh ≈ UPS kW × minutes ÷ 60 × 1.3
电池kWh ≈ UPS kW × 分钟数 ÷ 60 × 1.3
Earthing ≤ 1 Ω with mesh bonding, LPL I/II lightning protection and coordinated SPDs complete the electrical system.
接地≤1 Ω并网状等电位联结，I/II级防雷及多级SPD配合，构成完整电气系统。

## Slide 25: Mechanical & Cooling Systems
05
暖通与制冷系统
Every watt of IT becomes heat — cooling is the largest non-IT energy user.
IT的每一瓦都变成热量——制冷是最大的非IT能耗。

## Slide 26: Following the heat: from chip to atmosphere
热量路径：从芯片到大气
Chip & server
芯片与服务器
IT power → heat
IT电力→热量
Hot aisle
热通道
35–45 °C air
35–45 °C空气
CRAH / fan wall
精密空调/风墙
Coil 18/26 °C
盘管18/26 °C
Chilled water
冷冻水
18 °C supply
18 °C供水
Chiller
冷水机组
COP 6–7
COP 6–7
Condenser water
冷却水
32 / 37 °C
32 / 37 °C
Cooling tower
冷却塔
Evaporation
蒸发散热
Raising supply temperatures (ASHRAE 18–27 °C inlet, 18–20 °C chilled water) saves chiller energy and unlocks free cooling.
提高送风/供水温度（ASHRAE进风18–27 °C、冷冻水18–20 °C）可节省冷机能耗并实现自然冷却。
In tropical climates (wet-bulb ≈ 28 °C) free cooling is rare — efficient water-cooled chillers or liquid cooling matter most.
热带气候（湿球约28 °C）几乎无自然冷却——高效水冷冷机或液冷最为关键。
Air-cooled chillers or dry coolers avoid evaporative water use where water is scarce.
缺水地区可采用风冷冷机或干冷器以避免蒸发耗水。

## Slide 27: Choosing cooling by rack density
按机柜密度选择制冷方式
0
25
50
75
100
125
150
kW per rack 每柜千瓦
DX precision AC (CRAC)
直膨式精密空调
3–10 kW
CRAH / fan wall + containment
冷冻水精密空调/风墙+封闭
5–25 kW
In-row cooling
列间空调
15–40 kW
Rear-door heat exchanger
背板热交换器
20–75 kW
Direct-to-chip liquid (cold plate)
冷板式液冷
40–150+ kW
Immersion cooling
浸没式液冷
50–150+ kW
AI / GPU zone AI/GPU区间
Ranges are practical design envelopes; hybrid designs combine liquid for GPUs with air for the residual 10–25% of heat.
范围为实际设计区间；混合方案以液冷处理GPU热量，以风冷处理剩余10–25%热量。

## Slide 28: Central cooling plant & heat rejection
中央冷站与散热设备
Water-Cooled Centrifugal Chiller (Oil-Free Magnetic Bearing)
水冷离心式冷水机组（无油磁悬浮）
Produces chilled water for CRAHs/fan walls by rejecting heat to condenser water and cooling towers. Highest efficiency option for large plants in hot-humid climates.
为精密空调/风墙制取冷冻水，并通过冷却水和冷却塔排热。是湿热地区大型冷站效率最高的方案。
500 – 1,500 RT (1.75 – 5.3 MW) per unit; elevated chilled water 16–20 °C supply for data centres; N+1 or 2N.
Air-Cooled Chiller with Integrated Free Cooling
风冷冷水机组（带集成自然冷却）
Produces chilled water rejecting heat directly to air (no cooling tower, no evaporative water). Integrated free-cooling coils use cool ambient air when available.
直接向空气排热制取冷冻水（无冷却塔、无蒸发耗水）；环境温度低时由集成自然冷却盘管利用室外冷空气。
300 – 2,000 kW per unit; screw or centrifugal compressor; roof or yard mounted.
Cooling Tower (Induced-Draft)
冷却塔（机械引风式）
Rejects condenser heat to atmosphere by evaporation; the main consumer of water in a water-cooled plant.
通过蒸发将冷凝热排至大气；是水冷冷站的主要耗水设备。
Modular FRP/steel cells 1,000–2,500 RT each; design wet-bulb 28 °C (tropical), approach 3–4 K.
Thermal Energy Storage (Chilled-Water Buffer Tank)
蓄冷罐（冷冻水缓冲罐）
Provides continuous cooling during chiller restart after a power interruption (ride-through) and stabilises the plant.
在断电后冷机重启期间提供连续制冷（穿越），并稳定冷站运行。
Stratified steel tank sized for 10–15 min of full cooling load.

## Slide 29: Liquid cooling for AI: the CDU and two loops
AI液冷：CDU与两个环路
Heat rejection
散热设备
Dry coolers / towers
干冷器 / 冷却塔
CDU
冷量分配单元
Heat exchanger, pumps N+1, filters
换热器、N+1水泵、过滤器
GPU rack ≈ 130 kW GPU机柜
FWS loop 设施水
TCS loop 技术冷却
Cold-plate manifolds and quick disconnects on every server; 75–90% of heat to liquid at 30–45 °C.
每台服务器配冷板分液器及快插接头；75–90%热量以30–45 °C液体带走。
Why liquid?
为什么用液冷？
Water carries ≈ 3,500× more heat per volume than air.
单位体积水的携热量约为空气的3,500倍。
Warm-water loops cut or remove chiller energy (PUE ≈ 1.1–1.25).
温水环路减少或取消冷机能耗（PUE约1.1–1.25）。
Immersion submerges servers in dielectric fluid — up to 200 kW per tank.
浸没式将服务器浸入绝缘液——每槽可达200 kW。
Needs leak detection, coolant quality control and heavier floors.
需漏液检测、冷却液品质控制及更高楼面荷载。
ASHRAE liquid-cooling classes W17 → W45+ define facility water temperatures.
ASHRAE液冷等级W17→W45+定义设施水温。
Keep the TCS above dew point; N+1 CDUs per hall; A/B power to CDUs.
TCS温度保持在露点以上；每个机房CDU N+1；CDU采用A/B供电。

## Slide 30: How warm can servers run? ASHRAE thermal classes
服务器能承受多高温度？ASHRAE温度等级
0 °C
5 °C
10 °C
15 °C
20 °C
25 °C
30 °C
35 °C
40 °C
45 °C
50 °C
Recommended
推荐范围
18 – 27 °C
Class A1
A1级
15 – 32 °C
Class A2
A2级
10 – 35 °C
Class A3
A3级
5 – 40 °C
Class A4
A4级
5 – 45 °C
Class H1 (high density)
H1级（高密度）
15 – 25 °C
Server inlet air temperature. Recommended envelope for long-term reliability; allowable classes for short excursions per the equipment class. H1 (recommended 18–22 °C) applies to some high-density equipment — confirm with the IT vendor.
服务器进风温度。推荐范围用于长期可靠运行；允许范围依设备等级适用于短期偏离。H1（推荐18–22 °C）适用于部分高密度设备——需与IT厂商确认。

## Slide 31: Measuring efficiency: what makes up PUE
能效衡量：PUE的构成
Chart: Indicative annual PUE by design 不同设计的参考年均PUE
| Legacy enterprise 传统企业机房 | Tropical air-cooled 热带风冷 | Tropical water-cooled 热带水冷 | Liquid-cooled AI 液冷AI | Cold-climate free cooling 寒冷地区自然冷却
IT IT负载 | 1 | 1 | 1 | 1 | 1
Cooling 制冷 | 0.6 | 0.42 | 0.3 | 0.14 | 0.08
Electrical losses 电气损耗 | 0.15 | 0.07 | 0.07 | 0.07 | 0.06
Lighting & other 照明及其他 | 0.05 | 0.02 | 0.015 | 0.01 | 0.01
PUE = Total ÷ IT
Total facility energy divided by IT energy (ISO/IEC 30134-2).
设施总能耗除以IT能耗（ISO/IEC 30134-2）。
≈ 1.5
Global average reported by operators — flat for years (Uptime survey).
运营商报告的全球平均值——多年持平（Uptime调查）。
≤ 1.2 / 1.3
China GB 40879 PUE grade 1 / grade 2 limits.
中国GB 40879 PUE一级/二级限值。

## Slide 32: IT & Network Infrastructure
06
IT与网络基础设施
Racks, containment, cabling and connectivity — the physical home of compute.
机柜、通道封闭、布线与网络连接——计算设备的物理家园。

## Slide 33: The server rack: the basic unit of the white space
服务器机柜：白区的基本单元
rPDU A
rPDU B
42 – 52 U
Height (1U = 44.45 mm)
高度（1U = 44.45 mm）
600 / 800 mm
Width — 800 mm for network & AI
宽度——网络及AI用800 mm
1,070 – 1,200 mm
Depth for modern servers
现代服务器所需深度
1,360 – 1,800 kg
Static load rating (AI racks heavier)
静载能力（AI机柜更重）
≥ 80 %
Door perforation for airflow
门板开孔率保证气流
Good rack practice
机柜最佳实践
Blanking panels in every empty U and brush strips at cable entries.
所有空U位装盲板，线缆入口装毛刷条。
Two rPDUs fed from A and B sources for dual-corded equipment.
两条rPDU分别接A、B路，供双电源设备使用。
Hot- or cold-aisle containment around rack pods.
对机柜模块实施热通道或冷通道封闭。
Bond every rack to the telecom grounding system (TIA-607).
每个机柜接入通信接地系统（TIA-607）。
Label racks, PDUs and patch panels per TIA-606.
按TIA-606标识机柜、PDU和配线架。

## Slide 34: Network architecture: leaf-spine and AI fabrics
网络架构：叶脊架构与AI网络
Spine
脊交换机
Spine
脊交换机
Spine
脊交换机
Leaf
叶交换机
Leaf
叶交换机
Leaf
叶交换机
Leaf
叶交换机
Leaf
叶交换机
Servers 服务器
Servers 服务器
Servers 服务器
Servers 服务器
Servers 服务器
Core / border routers → carriers
核心/边界路由器→运营商
Every leaf connects to every spine → any server is two hops from any other; scale by adding leaves and spines.
每个叶交换机连接所有脊交换机→任意两台服务器间仅两跳；通过增加叶/脊扩展。
AI clusters add a second network
AI集群增加第二张网络
Back-end GPU fabric (InfiniBand or RoCE Ethernet) at 400–800 Gb/s per port.
后端GPU网络（InfiniBand或RoCE以太网），每端口400–800 Gb/s。
Rail-optimised, non-blocking (1:1) topology.
轨道优化、无阻塞（1:1）拓扑。
Thousands of short fibre links — plan cable trays and MPO trunks early.
成千上万条短光纤链路——尽早规划桥架与MPO主干。
Separate out-of-band management network.
独立带外管理网络。

## Slide 35: Structured cabling & carrier connectivity
综合布线与运营商连接
Single-mode fibre (OS2)
单模光纤（OS2）
Long reach backbone, campus and carrier links; 400G/800G optics.
长距离主干、园区及运营商链路；400G/800G光模块。
Multimode fibre (OM4 / OM5)
多模光纤（OM4/OM5）
Short links inside halls (≤ 100–150 m) with MPO trunks.
机房内短链路（≤100–150 m），采用MPO主干。
Copper Cat 6A
6A类铜缆
Management, OOB, BMS & security devices; PoE.
管理网、带外、BMS及安防设备；支持PoE。
Meet-Me Room
运营商交汇间
Two MMRs and ≥ 2 diverse entry points ≥ 20 m apart (Rated-3/4).
两个MMR及≥2个相距≥20 m的分离入口（Rated-3/4）。
Carrier-neutral ecosystem
运营商中立生态
Many carriers, internet exchanges and cloud on-ramps attract tenants.
多家运营商、互联网交换中心及云接入吸引租户。
Testing & labelling
测试与标识
100% OLTS/OTDR fibre tests, TIA-606 labels, 25-year system warranty.
光纤100% OLTS/OTDR测试，TIA-606标识，25年系统质保。

## Slide 36: Fire, Security & Monitoring
07
消防、安防与监控
Detect early, suppress without damage, control every door, see everything.
早期探测、无损灭火、管控每道门、全面可视。

## Slide 37: Fire protection: detect early, suppress without damage
消防：早期探测、无损灭火
Alert — Investigate
警告——人员调查
Action — Prepare, notify
行动——准备、通知
Fire 1 — Alarm, HVAC actions
火警1——报警、空调联动
Fire 2 — Release suppression (double-knock)
火警2——释放灭火（双重确认）
Aspirating smoke detection alarm levels → automatic actions 极早期烟雾探测报警等级→自动联动
Aspirating smoke detection
极早期吸气式烟雾探测
Samples air through pipes; detects smoke long before flames — essential with high airflow.
通过管网抽样空气，在明火前很早探测烟雾——高风速机房必备。
Addressable fire alarm
可寻址火灾报警
Alerts people and drives cause-and-effect: HVAC stop, door release, suppression release.
警示人员并执行联动：关闭空调、释放门禁、启动灭火。
Clean-agent / inert gas
洁净气体 / 惰性气体
Floods the room in 10–60 s without residue. Check HFC/PFAS rules for agent supply.
10–60 s内全淹没灭火、无残留。需关注HFC/PFAS法规对灭火剂供应的影响。
Pre-action sprinkler
预作用喷淋
Dry pipes fill only after detection + head operation — the hyperscale default.
干管仅在探测报警+喷头动作后充水——超大规模数据中心的常规做法。

## Slide 38: Physical security in layers: from fence to rack
分层物理安防：从围栏到机柜
1
Perimeter fence + PIDS
周界围栏+入侵探测
2
Gatehouse & vehicle barriers
门卫及车辆拦阻
3
Building envelope & entry
建筑外壳及入口
4
Lobby mantrap
大堂防尾随门
5
Data hall — card + biometric
机房——卡+生物识别
6
Cage / suite
笼位 / 包间
7
Rack e-lock
机柜电子锁
Each layer adds authentication and video verification; CCTV covers every door and aisle with ≥ 90-day retention.
每层增加认证与视频复核；CCTV覆盖所有门及通道，录像保存≥90天。

## Slide 39: Seeing everything: BMS, EPMS and DCIM
全面可视：BMS、EPMS与DCIM
Dashboard: NOC / SOC video wall, alarms, KPIs (PUE, WUE)
展示层：NOC/SOC大屏、报警、KPI（PUE、WUE）
Applications: BMS · EPMS · DCIM · security (VMS, ACS)
应用层：BMS·EPMS·DCIM·安防（视频、门禁）
Network: redundant OT network, BACnet/IP, Modbus TCP, SNMP, IEC 61850
网络层：冗余OT网络、BACnet/IP、Modbus TCP、SNMP、IEC 61850
Field: meters, PLC/DDC controllers, sensors, rPDUs, leak detection
现场层：表计、PLC/DDC控制器、传感器、rPDU、漏水检测
Building Management System (BMS)
楼宇自控系统（BMS）
Monitors and controls mechanical plant (chillers, pumps, CRAHs, ventilation), fuel, water, leak detection and alarms.
监控机械设备（冷机、水泵、精密空调、通风）、燃油、给水、漏水检测及报警。
Electrical Power Monitoring System (EPMS)
电力监控系统（EPMS）
High-resolution monitoring of the power chain — power quality, sequence of events, breaker status, energy and PUE metering.
对供电链进行高分辨率监测——电能质量、事件顺序、断路器状态、能耗及PUE计量。
Data Center Infrastructure Management (DCIM)
数据中心基础设施管理（DCIM）
Single source of truth for assets, space, power and cooling capacity, connectivity and change management; dashboards for KPIs (PUE, WUE, CUE).
资产、空间、电力与制冷容量、连接及变更管理的统一数据源；KPI仪表盘（PUE、WUE、CUE）。

## Slide 40: Supporting Systems & Project Lifecycle
08
支持系统与项目全生命周期
The “small” components, the building itself, and how a project is delivered.
“小”部件、建筑本身，以及项目如何交付。

## Slide 41: Secondary components that make or break reliability
决定可靠性的次要部件
Raised floor
架空地板
Cable trays & raceway
桥架与光纤槽道
Blanking panels & brush strips
盲板与毛刷条
Leak detection
漏水检测
LED & emergency lighting
LED及应急照明
Earthing & bonding
接地与等电位
Lightning & SPD
防雷与浪涌保护
Water treatment
水处理
VFDs & controls
变频器与控制
Environmental sensors
环境传感器
Loading dock & lift
装卸平台与货梯
Staging & spares store
预置区与备件库
Details and TPG for every item are in the companion Word specification.
各部件的详细要求及TPG见配套Word技术规范。

## Slide 42: Civil, structural & architectural requirements
土建、结构与建筑要求
15–25 kN/m²
White-space floor live load
白区楼面活荷载
4.5–6 m
Clear height (overhead services)
净高（上走线机电）
2 h
Fire separation between halls & plant
机房与设备间防火分隔
Ie 1.25–1.5
Seismic importance factor
抗震重要性系数
> 100-yr flood
Ground floor above design flood + freeboard
首层高于设计洪水位并留超高
≥ 3 t lift
Freight lift & 2.7–3 m door height
货梯及2.7–3 m门洞净高

## Slide 43: Project lifecycle: from idea to Ready-for-Service
项目全生命周期：从构想到投产
1
Strategy & Business Case
战略与商业论证
Demand, business model, target market, funding strategy.
需求、商业模式、目标市场、融资策略。
2
Feasibility & Site Selection
可行性研究与选址
Power & fibre availability, hazards, land, permits, CAPEX/OPEX, financial model.
电力与光纤可得性、灾害、土地、许可、投资/运营成本、财务模型。
3
Permits & Utility Applications
报批报建与公用事业申请
Grid connection, environmental approval, building permit, water rights.
电网接入、环境审批、建筑许可、取水许可。
4
Concept & Basis of Design
概念设计与设计依据
Tier, capacity, density, cooling and power architecture frozen.
确定Tier、容量、密度、制冷与供电架构。
5
Schematic & Detailed Design
方案及详细设计
Drawings, specifications, TPG, BOQ, tender documents; Tier design certification.
图纸、技术规范、TPG、工程量清单、招标文件；Tier设计认证。
6
Procurement
采购
Long-lead items first: transformers, generators, MV switchgear, UPS, chillers.
优先采购长周期设备：变压器、发电机、中压开关柜、UPS、冷机。
7
Construction & Installation
施工与安装
Civil/structural, building envelope, MEP installation, QA/QC.
土建/结构、建筑围护、机电安装、质量控制。
8
Testing & Commissioning (L1–L5)
测试与调试（L1–L5）
FAT → installation checks → start-up → functional tests → integrated systems test.
工厂测试→安装检查→单机启动→系统功能测试→综合系统测试。
9
Handover & Ready-for-Service
移交与投产
As-builts, O&M manuals, training, Tier facility certification, customer onboarding.
竣工图、运维手册、培训、Tier设施认证、客户入驻。
10
Operations & Optimisation
运营与优化
24/7 operations, maintenance, capacity management, PUE optimisation, expansions.
7×24运营、维护、容量管理、PUE优化、扩建。

## Slide 44: Commissioning levels L1–L5
调试等级L1–L5
L1
Factory Acceptance Test (FAT)
工厂验收测试
L2
Delivery & Installation Verification
到货及安装检查
L3
Start-up / Pre-functional
单机启动 / 预功能测试
Energise and start each component individually.
对各组件逐一通电启动。
L4
Functional Performance Test
系统功能性能测试
Test each system under load (load banks) incl. failure modes.
在负载（负载箱）下测试每个系统，包括故障模式。
L5
Integrated Systems Test (IST)
综合系统测试
All systems together: utility failure, generator start, UPS, cooling recovery.
所有系统联合测试：市电失效、发电机启动、UPS、制冷恢复。
L1–L3 prove each component; L4 tests each system under load-bank heat; L5 (IST) fails utility, generators, UPS and chillers together with the full heat load.
L1–L3验证每个组件；L4在负载箱热负荷下测试各系统；L5（综合测试）在满热负荷下联合模拟市电、发电机、UPS及冷机失效。
L1 at factory (FAT) · L2–L5 on site
L1在工厂（FAT）· L2–L5在现场

## Slide 45: What does it cost? Indicative CAPEX structure
投资多少？参考投资构成
Chart: Facility CAPEX by system (A05: Tier III, 10 MW) 按系统划分的设施投资
| Design, PM, commissioning & fees 设计、项目管理、调试及费用 | Site works & external 场地及室外工程 | BMS / EPMS / DCIM BMS/EPMS/DCIM | IT infrastructure IT基础设施 | Fire protection & security 消防与安防 | Civil, structural & architectural 土建、结构与建筑 | Mechanical / cooling 暖通/制冷 | Electrical systems 电气系统
Share of facility CAPEX | 0.06 | 0.04 | 0.02 | 0.04 | 0.04 | 0.18 | 0.2 | 0.42
Chart: Indicative CAPEX, USD million per MW IT 参考单位投资（百万美元/MW）
| Indonesia | Malaysia | Singapore | China | India | Japan | Australia | United States | Western Europe
USD M / MW | 10.5 | 11 | 14.5 | 7.5 | 7 | 15 | 12.5 | 11.5 | 12.5
Shell + MEP fit-out, Tier III, excluding land and IT hardware. Planning values — calibrate with a quantity surveyor for each project.
含建筑主体及机电装修，Tier III，不含土地及IT硬件。规划参考值——各项目需由造价顾问校准。

## Slide 46: Feasibility checklist: what decides a site and a project
可行性清单：决定场地与项目的因素
Power availability, cost & timeline (MVA, kV, tariff)
电力可得性、成本与时间（MVA、电压、电价）
Fibre routes, carriers, latency to users
光纤路由、运营商、到用户的时延
Natural hazards: flood, seismic, storms
自然灾害：洪水、地震、风暴
Land, zoning, permits & setbacks
土地、规划、许可及退界
Water availability & cooling strategy
水资源及制冷策略
Climate: free-cooling hours, design wet-bulb
气候：自然冷却时数、设计湿球温度
Regulation: data sovereignty, PDP law, incentives
法规：数据主权、个人数据保护法、激励政策
Market demand, pricing & anchor tenants
市场需求、定价及锚定租户
Skilled workforce & O&M partners
技术人员及运维合作伙伴
CAPEX, OPEX, IRR & financing
投资、运营成本、IRR及融资
Sustainability: renewables, PUE/WUE targets
可持续：可再生能源、PUE/WUE目标
Schedule & long-lead equipment
进度及长周期设备

## Slide 47: Sustainability is now a design requirement
可持续性已成为设计要求
415 TWh
Data-centre electricity use in 2024 (IEA)
2024年数据中心用电量（IEA）
× 2 by 2030
Projected growth, driven by AI (IEA base case)
预计增长，主要由AI驱动（IEA基准情景）
> 80%
Green-power target for new China hub DCs (2025)
中国新建枢纽数据中心绿电目标（2025）
Energy efficiency
能效
Higher temperatures, economisers, liquid cooling, efficient UPS → lower PUE.
提高温度、自然冷却、液冷、高效UPS→降低PUE。
Renewable power
可再生能源
Green tariffs, PPAs, RECs and on-site solar (e.g. PLN green energy products).
绿电电价、购电协议、绿证及屋面光伏（如PLN绿电产品）。
Water stewardship
水资源管理
Closed loops, dry coolers, recycled water; track WUE.
闭式环路、干冷器、再生水；追踪WUE。
Heat reuse & circularity
余热利用与循环
District heating, low-GWP refrigerants, embodied-carbon reduction.
区域供暖、低GWP冷媒、减少隐含碳。

## Slide 48: Bilingual glossary of key terms
关键术语中英对照
Term 术语 | Meaning 含义
PUE 电能利用效率 | Power Usage Effectiveness = total facility energy ÷ IT energy (ideal 1.0). 总设施能耗÷IT能耗（理想值1.0）。
WUE 水利用效率 | Water Usage Effectiveness = site water (L) ÷ IT energy (kWh). 场地用水量（L）÷IT能耗（kWh）。
UPS 不间断电源 | Uninterruptible Power Supply bridging power until generators start. 在发电机启动前桥接供电的不间断电源。
ATS 自动转换开关 | Automatic Transfer Switch — transfers load between two power sources. 在两路电源之间自动切换负荷的开关。
STS 静态转换开关 | Static Transfer Switch switching between two UPS sources in < 4 ms. 在<4 ms内于两路UPS间切换的静态开关。
PDU 列头配电柜 | Power Distribution Unit feeding racks from UPS. 从UPS向机柜供电的配电单元。
CRAH 冷冻水型精密空调 | Computer Room Air Handler using chilled water coils. 使用冷冻水盘管的机房空气处理机。
CDU 冷量分配单元 | Coolant Distribution Unit separating facility water from the technology cooling loop. 将设施水与技术冷却环路隔离的冷却液分配单元。
Term 术语 | Meaning 含义
CAC / HAC 冷/热通道封闭 | Cold- or hot-aisle containment separating supply and exhaust air. 隔离送风与排风的冷通道或热通道封闭。
MMR 运营商交汇间 | Meet-Me Room where carriers interconnect with tenants. 运营商与租户进行互联的房间。
DCIM 数据中心基础设施管理 | Software managing assets, capacity, power and environment. 管理资产、容量、电力及环境的软件。
BMS 楼宇自控系统 | Building Management System for mechanical & environmental monitoring/control. 用于机械及环境监控的楼宇管理系统。
IST 综合系统测试 | Integrated Systems Test — Level 5 commissioning of all systems together. 所有系统联合进行的第5级调试。
RFS 可交付使用 | Ready For Service — date capacity is available to customers. 容量可向客户交付使用的日期。
Concurrent maintainability 可同时维护 | Ability to maintain any component/path without IT impact (Tier III). 可维护任一组件/路径而不影响IT（Tier III）。
TPG 技术参数保证表 | Technical Particulars & Guarantees — bidder-guaranteed equipment data. 投标人保证的设备技术参数表。

## Slide 49: Project Development: Technical & Commercial
09
项目开发：技术与商业
What a 2026 Indonesian data center project must get right — power, platforms, cooling, storage, cost, returns, schedule and permits.
2026年印尼数据中心项目的关键：电力、平台、制冷、储能、投资、回报、进度与许可。

## Slide 50: Indonesia 2026: where data centers are being built
2026年印尼：数据中心建在哪里
Established hubs
成熟枢纽
Batam (Nongsa / Kabil) · Jakarta (in-city) · Bekasi – Cikarang · Karawang · Tangerang
巴淡（农萨/卡比尔） · 雅加达市区 · 勿加泗-芝加朗 · 卡拉旺 · 唐格朗
Emerging locations
新兴地点
Medan / Kuala Namu · Bintan · Bogor – Sentul · Bandung (highland) · Serang – Cilegon · Semarang – Kendal · Surabaya – Gresik · Denpasar · Balikpapan · IKN Nusantara · Makassar
棉兰/瓜拉纳穆、民丹、茂物-森图尔、万隆（高原）、西冷-芝勒贡、三宝垄-肯德尔、泗水-锦石、登巴萨、巴厘巴板、努桑塔拉新首都、望加锡
AI campuses of several hundred MW are now announced around Jakarta (e.g. BDx Jatiluhur ≈ 500 MW, Digital Edge CGK ≈ 500 MW, public reports): power availability decides the site first.
雅加达周边已公布数百MW级AI园区（如BDx佳蒂卢胡尔约500 MW、Digital Edge CGK约500 MW，公开报道）：电力可得性成为选址首要因素。
The location sets the design climate (lowland wet-bulb ≈ 27–28 °C, highland ≈ 23–24 °C), seismic and flood exposure, land and water price, the provincial minimum wage and the construction logistics factor applied to CAPEX.
地点决定设计气候（低地湿球约27–28 °C，高原约23–24 °C）、地震及洪水风险、土地与水价、省级最低工资及投资的施工物流系数。
Real projects in Indonesia (public information) 印尼真实项目（公开信息） | MW | Status 状态
BDx — CGK4 AI Campus, Jatiluhur BDx——CGK4 AI园区（佳蒂卢胡尔） | ≈ 500 | Phase 1 operating; multi-phase
Digital Edge — CGK Campus, Jakarta Digital Edge——雅加达CGK园区 | ≈ 500 | Planned / phased
EdgeConneX — Jakarta campus (incl. former GTN Cikarang) EdgeConneX——雅加达园区（含原GTN芝加朗） | ≈ 200 | Operating; expanding
Princeton Digital Group — JC3 Greater Jakarta 普林斯顿数字集团——JC3大雅加达园区 | ≈ 120 | Under construction (phase 1 target Q4 2026)
DCI Indonesia — Cibitung Campus DCI Indonesia——芝比通园区 | ≈ 73 | Operating / expanding
DayOne — Batam Campus (Nongsa Digital Park) DayOne——巴淡园区（农萨数字园） | ≈ 72 | Phased; buildings 1–2 operating
NeutraDC Nxera Batam (Telkom × Singtel × Medco) NeutraDC Nxera巴淡（Telkom×新电信×Medco） | ≈ 54 | BTM-1 topped off Oct 2025; phase 1 targeted 2026
NTT — Jakarta 3 (JKT3) NTT——雅加达3号（JKT3） | ≈ 45 | Operating
Digital Edge — EDGE2 Jakarta (Kuningan) Digital Edge——EDGE2雅加达（库宁安） | ≈ 23 | Operating since Feb 2024
Pusat Data Nasional (PDN) — Cikarang 国家数据中心（PDN）——芝加朗 | ≈ 20 | Completed 2025; phased commissioning
Telkom neuCentrIX — edge data center network Telkom neuCentrIX——边缘数据中心网络 | ≈ 6.0 | Operating; expanding
Space DC — JAK2 (containerised prefabricated) Space DC——JAK2（集装箱式预制） | ≈ 1.5 | Operating (2021)

## Slide 51: PLN power: connection, tariff and timeline
PLN供电：接入、电价与时间
Maximum demand 最大需量 | Connection 接入方式 | Tariff 电价
≤ 2 MVA | LV / MV service ≤ 20 kV 低压/中压供电≤20 kV | B-3 / I-3 TM
2–30 MVA | MV 20 kV, dedicated feeders 中压20 kV专用馈线 | B-3 / I-3 TM
30–300 MVA | HV 150 kV with on-site substation 高压150 kV，自建变电站 | I-4 TT
> 300 MVA | EHV 500 kV / several 150 kV substations 超高压500 kV/多座150 kV变电站 | I-4 TT
PLN tariff (Q4 2026) 电价 | LWBP Rp/kWh | K | 24/7 Rp/kWh
B-3 / TM — business, MV > 200 kVA B-3/中压——商业用电>200 kVA | 1,114.74 | 1.4 | 1,207.6
I-3 / TM — industrial, MV > 200 kVA I-3/中压——工业用电>200 kVA | 1,114.74 | 1.4 | 1,207.6
I-4 / TT — industrial, HV ≥ 30,000 kVA I-4/高压——工业用电≥30,000 kVA | 996.74 | 1 | 996.7
REC ≈ Rp35,000/MWh · FX ≈ Rp17,900/USD · grid ≈ 0.79 tCO₂e/MWh
Apply to PLN at feasibility stage: connection agreement and energisation take ≈ 16 months in the benchmark programme and are usually on the critical path.
在可研阶段即向PLN申请：基准进度中接入协议及送电约需16个月，通常位于关键路径。
The connection voltage follows maximum demand (IT × design-day PUE ÷ power factor 0.95): ≤ 30 MVA at 20 kV (TM), 30–300 MVA at 150 kV (TT) with an on-site substation; Tier III+ takes two independent feeds.
接入电压取决于最大需量（IT×设计日PUE÷功率因数0.95）：≤30 MVA采用20 kV（TM），30–300 MVA采用150 kV（TT）并自建变电站；Tier III及以上采用两路独立进线。
Tariff class follows the connection (Q4 2026): TM B-3 / I-3 Rp1,114.74/kWh off-peak, ≈ Rp1,207.6/kWh blended for a 24/7 load (peak factor K ≈ 1.4); TT I-4 Rp996.74/kWh flat.
电价类别取决于接入方式（2026年第四季度）：中压B-3/I-3低谷1,114.74印尼盾/kWh，24/7负荷加权约1,207.6印尼盾/kWh（高峰系数K≈1.4）；高压I-4统一996.74印尼盾/kWh。
Green power is inexpensive: PLN RECs ≈ Rp35,000/MWh (≈ USD 2.0/MWh); add rooftop solar (Permen ESDM 2/2024) and PPAs where RUPTL allows. Grid emission factor ≈ 0.79 tCO₂e/MWh.
绿电成本较低：PLN绿证约35,000印尼盾/MWh（约2.0美元/MWh）；可增加屋顶光伏（Permen ESDM 2/2024）及RUPTL允许的购电协议。电网排放因子约0.79 tCO₂e/MWh。
Weaker regional grids (outside JAMALI) call for more generator fuel (+24 h medium, +48 h low reliability) and a BESS for sites ≥ 5 MW.
区域电网较弱（JAMALI以外）时需增加发电机燃油（中等可靠性+24 h，低可靠性+48 h），≥5 MW站点配置储能。

## Slide 52: IT platforms 2026: from 10 kW to 600 kW per rack
2026年IT平台：每柜10 kW至600 kW
Platform 平台 | Cooling | kW design / peak | Liquid | Rack W×D · U | kg | GPU
NVIDIA GB300 NVL72 rack-scale system NVIDIA GB300 NVL72机架级系统 | DLC | 135 / 155 | 90 % | 600×1068 · 48U | 1,500 | 72
NVIDIA Vera Rubin NVL144 / VR200 (provisional) NVIDIA Vera Rubin NVL144 / VR200 | DLC | 190 / 230 | 95 % | 600×1068 · 48U | 1,700 | 72
NVIDIA Rubin Ultra NVL576 “Kyber” (provisional) NVIDIA Rubin Ultra NVL576“Kyber” | DLC | 600 / 600 | 98 % | 1200×1200 · 48U | 3,000 | 576
AMD Instinct MI355X — liquid-cooled 8-GPU nodes (provisional) AMD Instinct MI355X——液冷8卡节点 | DLC | 110 / 125 | 85 % | 600×1200 · 48U | 1,300 | 64
NVIDIA DGX/HGX B300 — air-cooled NVIDIA DGX/HGX B300——风冷 | RDHX | 58 / 62 | 60 % | 600×1200 · 48U | 1,100 | 32
NVIDIA DGX/HGX H100–H200 — air-cooled NVIDIA DGX/HGX H100–H200——风冷 | RDHX | 41 / 44 | 50 % | 600×1200 · 48U | 950 | 32
Huawei CloudMatrix 384 华为CloudMatrix 384 | RDHX | 35 / 45 | 50 % | 800×1200 · 47U | 1,100 | 24
Inference GPU servers 推理GPU服务器 | AIR | 20 / 24 | – | 600×1200 · 48U | 800 | 24
High-density CPU / multi-node / blade 高密度CPU/多节点/刀片服务器 | AIR | 25 / 30 | – | 600×1200 · 48U | 950 | –
General-purpose 1U/2U servers 通用1U/2U服务器 | AIR | 10 / 12 | – | 600×1200 · 48U | 750 | –
Provision power above nominal: OEMs suggest ≈ 190 kW of busway per GB300 rack; next generations (Vera Rubin ≈ 190 kW, Kyber ≈ 600 kW, provisional) need 800 V DC-ready distribution paths and heavier floors.
供电容量须高于额定值：OEM建议每台GB300机柜约190 kW母线容量；下一代（Vera Rubin约190 kW、Kyber约600 kW，暂定）需预留800 V直流配电路径及更高楼面承载。

## Slide 53: Counting IT equipment: positions, cabinets, GPU systems, PDUs
机柜计数：机柜位、机柜、GPU系统与PDU
Term 术语 | Definition and counting rule 定义与计数规则
Rack position 机柜位 | One physical place for a rack in the white space, with its power feeds, cooling and floor capacity. Total racks = standard + high-density positions. 白区内放置一个机柜的物理位置，含供电、制冷及楼面承载。机柜总数=标准+高密度机柜位。
Cabinet (IT-01) 机柜（IT-01） | Steel enclosure, e.g. 48U 600 × 1,200 mm. Standard cabinets are facility supply; integrated rack-scale AI racks and OCP racks arrive with the IT, so only the position is provided. 钢制外壳，如48U 600×1,200 mm。标准机柜由设施供货；机架级集成AI机柜及OCP机柜随IT到货，设施仅提供机柜位。
GPU / AI system (IT-08) GPU/AI系统（IT-08） | An 8-GPU server (4–8 per rack) or a rack-scale system (1 per rack, e.g. NVL72 with 72 GPUs). IT scope inside the high-density positions — never additional racks. 8卡服务器（每柜4–8台）或机架级系统（每柜1套，如NVL72含72颗GPU）。属于高密度机柜位内的IT范围——绝不是额外机柜。
Rack PDU (EL-14) 机柜PDU（EL-14） | Counted per feed: 2 per standard rack (A + B); 2 per feed (4 per rack) above ≈ 43 kW; none where power shelves are used. 按每路计数：标准机柜每柜2条（A+B）；约43 kW以上每路2条（每柜4条）；使用电源架时不需要。
Power shelf 电源架 | AC/DC shelves feeding a DC busbar inside AI and OCP racks (e.g. 8 × 33 kW, 50 V or 48 V DC); replaces rack PDUs. AI及OCP机柜内为直流母排供电的交直流电源架（如8×33 kW、50 V或48 V直流）；替代机柜PDU。
Busway tap-off (EL-13) 母线插接箱（EL-13） | Plug-in unit on the overhead busway, one per rack per feed (more for high-density racks); feeds rack PDUs or power shelves. 上走线母线上的插接单元，每柜每路一个（高密度机柜更多）；为机柜PDU或电源架供电。
A05 Retail colocation | Qty | Basis 依据
Rack positions (total) 机柜位（合计） | 676 | 608 standard + 68 high-density
IT-01 standard cabinets IT-01 标准个机柜 | 608 | Standard racks: General-purpose 1U/2U servers (virtualisation, databases), 10.0 kW — facility supply
IT-01 high-density cabinets IT-01 高密度个机柜 | 68 | High-density cabinets: 58 kW — facility supply
IT-08 GPU / AI systems IT-08 GPU/AI系统 | 272 | 8 GPUs per system · 2,176 GPUs inside the 68 HD racks above — IT scope, reference (not additional racks)
EL-14 rack PDUs EL-14 机柜PDU | 1,488 | 608 standard racks × 2 + 68 HD racks × 4 — A + B feeds
A07 Hyperscale cloud campus | Qty | Basis 依据
Rack positions (total) 机柜位（合计） | 3,175 | 2,857 standard + 318 high-density
IT-01 standard positions IT-01 标准个机柜位 | 2,857 | Standard rack positions: OCP Open Rack v3 cloud rack (21″, 48 V busbar), 20.0 kW — racks arrive integrated with the IT (rack-level integration)
IT-01 high-density positions IT-01 高密度个机柜位 | 318 | High-density rack positions: integrated cabinet arrives with the IT system (135 kW)
IT-08 GPU / AI systems IT-08 GPU/AI系统 | 318 | 72 GPUs per system · 22,896 GPUs inside the 318 HD racks above — IT scope, reference (not additional racks)
EL-14 rack PDUs EL-14 机柜PDU | 0 | Not required — power shelves fed by busway tap-offs

## Slide 54: Choosing the cooling: density, climate and a weighted matrix
选择制冷：密度、气候与加权矩阵
Technology 技术 | ≤ kW/rack | Best for 适用
DX precision AC (CRAC) 直膨式精密空调（CRAC） | 10 | Simple, no water; for small rooms and edge sites. 简单、无水系统；适合小型机房和边缘站点。
Air-cooled chillers + CRAH / fan wall 风冷冷水机组 + 冷冻水精密空调 / 风墙 | 25 | No evaporative water use; good where water is scarce. 无蒸发耗水；适合缺水地区。
Water-cooled chillers + cooling towers + CRAH / fan wall 水冷冷水机组 + 冷却塔 + 精密空调 / 风墙 | 25 | Most efficient compressor-based plant for large sites in hot-humid climates; uses water. 湿热地区大型站点效率最高的压缩机制冷方案；需耗水。
Indirect evaporative cooling (IEC) 间接蒸发冷却（IEC） | 20 | Very low PUE in dry/temperate climates; limited benefit in tropical climates. 干燥/温和气候下PUE极低；热带气候效果有限。
Direct liquid cooling (cold plate) + residual air 冷板式液冷 + 余热风冷 | 150 | Required for AI/GPU racks above ~40 kW; warm-water loops enable chiller-less heat rejection. 约40 kW以上AI/GPU机柜必需；温水环路可实现无冷机散热。
Immersion cooling 浸没式液冷 | 200 | Lowest PUE; specialised IT, fluid handling and floor loading considerations. PUE最低；需专用IT、冷却液管理并考虑楼面荷载。
Lowland tropical wet-bulb (≈ 27–28 °C) leaves almost no free-cooling hours, so evaporative / indirect-evaporative systems lose their advantage; highland sites (≈ 23–24 °C) and warm-water liquid cooling recover economiser hours.
低地热带湿球（约27–28 °C）几乎没有自然冷却时数，蒸发/间接蒸发冷却失去优势；高原站点（约23–24 °C）及温水液冷可恢复节能器时数。
Typical outcome: DX CRAC below ≈ 1 MW; air-cooled chillers + CRAH to ≈ 5 MW; water-cooled chillers + towers for larger air-cooled halls; direct-to-chip liquid cooling whenever racks exceed ≈ 25–40 kW.
典型结果：约1 MW以下采用直膨精密空调；约5 MW以下采用风冷冷机+精密空调；更大的风冷机房采用水冷冷机+冷却塔；机柜超过约25–40 kW时采用冷板液冷。
Chart: Annual PUE of the benchmark designs 基准设计年均PUE
| A11 Regional edge | A10 AI gigawatt-class campus | A09 Highland high-efficiency DC | A08 AI factory | A07 Hyperscale cloud campus | A06 Wholesale / build-to-suit | A05 Retail colocation | A04 Modular prefabricated | A03 Government / sovereign | A02 Enterprise | A01 Edge micro
Annual PUE | 1.38 | 1.18 | 1.23 | 1.19 | 1.28 | 1.28 | 1.39 | 1.5 | 1.51 | 1.51 | 1.5
Decision weights: efficiency 28 · water 12 (25 if constrained) · scale 18 · CAPEX 14 · maturity 14 · IT fit 14
决策权重：能效28·用水12（受限时25）·规模18·投资14·成熟度14·IT适配14
PUE benchmarks: Uptime global average ≈ 1.5; tropical air-cooled new builds 1.35–1.45; liquid-cooled AI 1.15–1.25; China GB 40879 grade 2 ≤ 1.30. The benchmark designs range 1.18–1.51.
PUE基准：Uptime全球平均约1.5；热带风冷新建1.35–1.45；液冷AI 1.15–1.25；中国GB 40879二级≤1.30。基准设计范围1.18–1.51。

## Slide 55: Direct liquid cooling: what the facility must provide
冷板液冷：设施需要提供什么
GPU cold plates
GPU冷板
≈ 90 % of rack heat
Rack manifold & QDs
机柜分液器与快插
dripless · leak detection
CDU (TCS ↔ FWS)
CDU（TCS↔FWS）
approach ≈ 3 K · N+1
Facility water
设施水
dry-bulb + ≈ 7 K
Dry coolers + trim
干冷器+补冷
little or no water
Technology cooling system (TCS): ≈ 35–40 °C supply to the cold plates, ≈ 10 K rise; filtered (25–50 µm) PG25 or inhibited water, dripless quick disconnects and leak detection under every rack row.
技术冷却系统（TCS）：冷板供液约35–40 °C，温升约10 K；过滤（25–50 µm）的PG25或缓蚀水、无滴漏快插接头，每排机柜下设漏水检测。
Coolant distribution units (CDU): approach ≈ 3 K, N+1 pumps and units, one CDU of ≈ 1,500 kW (facility) or ≈ 1.3 MW in-row per ≈ 8 GB300 racks; controls on flow and differential pressure.
冷却液分配单元（CDU）：趋近温度约3 K，水泵及机组N+1；设施级CDU约1,500 kW，或列间约1.3 MW服务约8台GB300机柜；按流量及压差控制。
Facility water system (FWS) ≈ 7 K above outdoor dry-bulb, rejected by dry coolers (little or no water) with chiller trim for the hottest hours; ≈ 10–20% residual heat still goes to air (CRAH / fan walls).
设施水系统（FWS）比室外干球高约7 K，由干冷器（几乎不耗水）散热，最热时段由冷机补冷；仍有约10–20%余热需由空气（精密空调/风墙）处理。
Commission the liquid loops like process piping: flushing and cleanliness, pressure tests, coolant chemistry baseline, CDU failover and leak-response tests at L4–L5.
液冷环路按工艺管道调试：冲洗与清洁、压力试验、冷却液化学基线，并在L4–L5进行CDU切换及漏水响应测试。

## Slide 56: Energy storage: UPS batteries and BESS
储能：UPS电池与电池储能系统
UPS batteries — ride-through to the generators
UPS电池——过渡至发电机
UPS batteries: LFP lithium-ion is standard for new Indonesian data centers (≈ 1/3 of the footprint and weight of VRLA, 12–15 year life, built-in BMS); design to NFPA 855 and UL 9540A test data.
UPS电池：磷酸铁锂已成为印尼新建数据中心标配（占地及重量约为铅酸的1/3、寿命12–15年、内置BMS）；按NFPA 855及UL 9540A试验数据设计。
UPS autonomy proposed: 5 min with LFP (10 min Tier IV), 10 min with VRLA (15 min Tier IV) — generators start and accept load in 10–15 s; AI factories 5 min.
建议UPS后备：磷酸铁锂5 min（Tier IV 10 min），铅酸10 min（Tier IV 15 min）——发电机10–15 s启动接带负荷；AI算力中心5 min。
BESS — buffer, support and peak shaving
储能——缓冲、支撑与削峰
BESS is proposed for AI factories (≈ 15% of IT MW for 1 h, buffering synchronous GPU load swings), weaker grids ≥ 5 MW (≈ 10% for 2 h) and renewable-heavy hyperscale / wholesale sites (≈ 10% for 2 h).
储能建议用于：AI算力中心（IT MW约15%、1 h，缓冲GPU同步负荷波动）、≥5 MW的弱电网站点（约10%、2 h）及高可再生比例的超大规模/批发站点（约10%、2 h）。
Planning values: LFP containers ≈ 5 MWh each, ≈ USD 280/kWh installed incl. PCS; peak-shaving savings arise on TM tariffs (peak/off-peak), not on flat TT tariffs. A BESS never replaces generators or UPS.
规划参数：每个LFP集装箱约5 MWh，含PCS安装约280美元/kWh；削峰收益仅在中压分时电价下产生，高压统一电价下无此收益。储能不替代发电机或UPS。
Benchmark with BESS 配置储能的基准设计 | IT MW | BESS MW / MWh | Containers | CAPEX
A03 · Government / sovereign data center — 5 MW | 5 | 0.5 / 1.0 | 1 | USD 0.3 M
A06 · Wholesale / build-to-suit — 30 MW | 30 | 3.0 / 6.0 | 2 | USD 1.7 M
A07 · Hyperscale cloud campus — 100 MW | 100 | 10.0 / 20.0 | 4 | USD 5.6 M
A08 · AI factory — 50 MW liquid-cooled | 50 | 7.5 / 7.5 | 2 | USD 2.1 M
A09 · Highland high-efficiency DC — 20 MW | 20 | 2.0 / 4.0 | 1 | USD 1.1 M
A10 · AI gigawatt-class campus — 600 MW | 600 | 90.0 / 90.0 | 18 | USD 25.2 M
A11 · Regional edge data center — 25 MW | 25 | 2.5 / 5.0 | 1 | USD 1.4 M

## Slide 57: Resilience target → redundancy, autonomy and cost
韧性目标→冗余、后备时间与投资
Tier | Redundancy 冗余 | Availability | CM | FT | Fuel (JAMALI) | UPS (LFP) | CAPEX factor | USD M/MW*
Tier I Tier I | N | 99.671 % | – | – | 12 h | 5 min | × 0.62 | 6.8
Tier II Tier II | N+1 | 99.741 % | – | – | 24 h | 5 min | × 0.78 | 8.6
Tier III Tier III | N+1 | 99.982 % | ✓ | – | 24 h | 5 min | × 1.00 | 11.0
Tier IV Tier IV | 2N / 2(N+1) | 99.995 % | ✓ | ✓ | 48 h | 10 min | × 1.28 | 14.1
* Retail colocation benchmark (A05, 10 MW, Bekasi–Cikarang) re-run at each Tier. 零售托管基准（A05，10 MW，勿加泗-芝加朗）按各等级重算。
Tier follows workload criticality: mission-critical ≥ 2 MW → Tier IV (≈ SNI 8799 Strata IV, 2N with automatic failover); business-critical → Tier III (Indonesian market standard); small sites < 0.5 MW → Tier II.
等级取决于业务关键程度：≥2 MW关键任务→Tier IV（≈SNI 8799 Strata IV，2N自动切换）；业务关键→Tier III（印尼市场标准）；<0.5 MW小型站点→Tier II。
Generator fuel: 12 / 24 / 24 / 48 h for Tier I–IV, +24 h on medium-reliability and +48 h on low-reliability grids (max 96 h). Uptime requires ≥ 12 h at N load; TIA-942 references 72 h (Rated-3) and 96 h (Rated-4).
发电机燃油：Tier I–IV分别12/24/24/48 h，中等可靠性电网+24 h、低可靠性电网+48 h（最多96 h）。Uptime要求N负荷下≥12 h；TIA-942参考72 h（Rated-3）及96 h（Rated-4）。

## Slide 58: CAPEX: how USD 10–15 M per MW is built up
投资：每MW 1,000–1,500万美元如何构成
USD 10.5 M/MW
Greater Jakarta benchmark (Tier III, 10–30 MW)
大雅加达基准（Tier III，10–30 MW）
× 0.95 – 1.4
Location logistics factor
地点物流系数
× 0.62 – 1.28
Tier I – IV
Tier I–IV
× 1.45 – 0.87
Scale (< 1 MW … > 300 MW)
规模（<1 MW……>300 MW）
× 0.95 – 1.10
Cooling (DX … immersion)
制冷（直膨……浸没）
+ 15 %
Contingency + utility, land, BESS
不可预见费+电网接入、土地、储能
Chart: Facility CAPEX by system (A05) 按系统划分的设施投资
| Design, PM, commissioning & fees | Site works & external | BMS / EPMS / DCIM | IT infrastructure | Fire protection & security | Civil, structural & architectural | Mechanical / cooling | Electrical systems
Share | 0.06 | 0.04 | 0.02 | 0.04 | 0.04 | 0.18 | 0.2 | 0.42
Chart: USD M per MW IT, benchmark designs 基准设计单位投资
| A01 | A02 | A03 | A04 | A05 | A06 | A07 | A08 | A09 | A10 | A11
USD M/MW | 11.9 | 12 | 15.3 | 13.6 | 11 | 11.3 | 10.2 | 11.1 | 11.3 | 10.2 | 11.4

## Slide 59: OPEX: energy is the dominant running cost
运营成本：电费是最主要的运行成本
Chart: Stabilised OPEX split — A05 retail colocation 10 MW 稳定期运营成本构成
| Energy 电费 | Maintenance 维护 | Staff 人员 | Insurance 保险 | Water 水费 | RECs 绿证 | Other G&A 其他
OPEX | 7110916 | 1323000 | 666000 | 275625 | 141474 | 206096 | 275625
USD 10.0 M / yr · 105.4 GWh
Energy is ≈ 63–73% of stabilised OPEX across the benchmark designs — PUE and the tariff class are the biggest levers.
各基准设计中电费约占稳定期运营成本的63–73%——PUE及电价类别是最大的影响因素。
Planning ratios: maintenance ≈ 1.2% of facility CAPEX per year (+1.5% of BESS CAPEX), insurance & property ≈ 0.25%, other G&A ≈ 0.25%; staff = FTE × cost (a 24/7 post needs ≈ 5.2 FTE).
规划比例：维护约为设施投资的1.2%/年（储能另加其投资的1.5%），保险及物业约0.25%，其他管理费约0.25%；人员=人数×单价（每个7×24岗位约需5.2人）。
Water follows the cooling choice (cooling towers evaporate ≈ 1.5 L per kWh of heat); RECs to match 100% of consumption add little cost.
用水取决于制冷方案（冷却塔每kWh热量约蒸发1.5 L）；以绿证匹配100%用电增加的成本很小。
Lever: 0.10 lower PUE on 10 MW at 85 % utilisation saves ≈ 7,446 MWh ≈ USD 0.50 M per year at the TM tariff.
杠杆：10 MW、85%利用率下PUE降低0.10，每年可节省约7,446 MWh，按中压电价约0.50百万美元。

## Slide 60: Business case: lease returns or cost of ownership
商业模式：租赁回报或拥有成本
Facility type 设施类型 | USD/kW·mo
Retail Colocation 零售型托管 | 165
Wholesale / Build-to-Suit 批发型 / 定制建设 | 135
Hyperscale / Cloud 超大规模 / 云 | 125
AI Factory / HPC AI算力中心 / 高性能计算 | 185
Edge / Micro Data Center 边缘 / 微型数据中心 | 190
Modular / Prefabricated 模块化 / 预制式 | 150
Enterprise (Owner-operated) 企业自建（自用） | 165
Government / Sovereign 政府 / 主权数据中心 | 165
Major hub · excl. power · Batam × 0.95 · emerging × 0.9
Chart: Project IRR incl. exit, unlevered after tax (WACC ≈ 10 %) 项目IRR（含终值，无杠杆税后）
| A01 Edge micro | A05 Retail colocation | A06 Wholesale / build-to-suit | A07 Hyperscale cloud campus | A08 AI factory | A09 Highland high-efficiency DC | A10 AI gigawatt-class campus | A11 Regional edge
IRR | 5.9 | 8 | 7.4 | 7 | 11 | 6.8 | 11.5 | 9.6
Lease (colocation, wholesale, hyperscale, AI): monthly price per kW IT excluding power, utilisation ramp (≈ 2 years pre-leased hyperscale / AI, ≈ 4–5 years retail colocation) to 85–90%, power passed through at cost.
租赁（托管、批发、超大规模、AI）：按每kW IT月租计价（不含电费），利用率爬坡（预租超大规模/AI约2年，零售托管约4–5年）至85–90%，电费按成本转嫁。
Returns are unlevered and after 22% corporate tax, over 20 years, with a conservative exit at 10–12× EBITDA (regional transactions are often 15–25×); WACC ≈ 10% (USD) for developers, ≈ 8% for owner-occupiers.
回报按无杠杆、22%企业所得税后、20年计算，保守终值为10–12倍EBITDA（区域交易常为15–25倍）；开发商WACC约10%（美元），自用业主约8%。
Electricity resale with a markup requires an IUPTL licence — otherwise pass power through at cost.
加价转售电力需持IUPTL许可——否则电费按成本转嫁。

## Slide 61: Schedule: what sets Ready-for-Service
进度：什么决定投产时间
M0
M6
M12
M18
M24
Feasibility, site selection & land
可行性研究、选址及土地
4 mo
Concept, schematic & detailed design
概念、方案及详细设计
7 mo
Permits (OSS-RBA, PKKPR, AMDAL/UKL-UPL, PBG)
许可（OSS-RBA、PKKPR、AMDAL/UKL-UPL、PBG）
9 mo
PLN connection agreement & energisation
PLN接入协议及送电
16 mo
Procurement of long-lead equipment
长周期设备采购
12 mo
Construction & MEP installation
施工及机电安装
15 mo
Testing & commissioning (L1–L5)
测试与调试（L1–L5）
3 mo
Ready for Service — Phase 1
第一期投产
1 mo
A05 retail colocation 10 MW, phase 1: 28 months to RFS A05零售托管10 MW第一期：至投产28个月
Programme to Ready-for-Service ranges from 18 months (edge) to 54 months (gigawatt-class campus) in the benchmark designs.
基准设计中至投产的工期从18个月（边缘）到54个月（吉瓦级园区）不等。
The PLN connection, permits (PKKPR, AMDAL / UKL-UPL, PBG) and long-lead equipment — HV/MV transformers and switchgear, generators, UPS, chillers and CDUs — set the critical path; freeze the single-line diagram early.
PLN接入、许可（PKKPR、AMDAL/UKL-UPL、PBG）及长周期设备——高/中压变压器及开关柜、发电机、UPS、冷机及CDU——决定关键路径；须尽早冻结单线图。
Prefabricated power skids and modules shorten site time for edge, modular and ≥ 50 MW AI projects; phase later capacity one year before it is needed.
预制电力撬块及模块可缩短边缘、模块化及≥50 MW AI项目的现场工期；后续容量在需求前一年建设。

## Slide 62: Permits & approvals in Indonesia (2026)
印尼许可与审批（2026年）
1
OSS-RBA business licence (PP 28/2025): NIB + standard certificate, KBLI 2025 code 63102
OSS-RBA经营许可（PP 28/2025）：NIB+标准证书，KBLI 2025代码63102
2
Spatial conformity KKPR / PKKPR for the site
场地空间用途符合性KKPR/PKKPR
3
Environmental approval: AMDAL or UKL-UPL (PP 22/2021)
环境审批：AMDAL或UKL-UPL（PP 22/2021）
4
Building approval PBG and certificate of function SLF (PP 16/2021)
建筑审批PBG及使用功能证书SLF（PP 16/2021）
5
PLN connection agreement & SLO (operation-worthiness certificate); captive power licence if on-site generation exceeds limits
PLN接入协议及SLO（运行合格证）；现场发电超限时办理自备电力许可
6
PSE registration (Permenkomdigi 5/2025); personal data protection (UU 27/2022)
PSE登记（Permenkomdigi 5/2025）；个人数据保护（UU 27/2022）
7
Fire safety approval (Permen PU 26/2008, local Damkar); K3 electrical (Permenaker 12/2015)
消防审批（Permen PU 26/2008、地方消防局）；电气K3（Permenaker 12/2015）
8
Groundwater / surface-water permits when abstracting water; generator emission compliance
取用地下/地表水时办理许可；发电机排放合规

## Slide 63: Top project risks and how to mitigate them
主要项目风险及应对
 | Risk 风险 | Mitigation 应对措施
H | A01: Project IRR (incl. exit value) 5.9% is below the discount rate 10%. A01：项目IRR（含终值）5.9%低于折现率10%。 | Review pricing, phasing, CAPEX and ramp-up assumptions. 复核定价、分期、投资及爬坡假设。
M | A01: Flood exposure at Surabaya – Gresik. A01：泗水-锦石存在洪水风险。 | Raise finished floor above the 100-year flood + freeboard, critical plant on upper levels, flood barriers. 室内地坪高于百年一遇洪水位并留超高，关键设备上置，设防洪挡板。
L | A01: RECs alone do not add new renewable capacity (additionality). A01：仅靠绿证无法新增可再生能源容量（额外性）。 | Combine PLN RECs with rooftop solar (PLTS Atap) and long-term PPAs as RUPTL allows. 结合PLN绿证、屋顶光伏及RUPTL允许的长期购电协议。
M | A02: Lithium-ion batteries / BESS introduce thermal-runaway fire risk. A02：锂电池/储能存在热失控火灾风险。 | LFP chemistry, UL 9540A-tested systems, off-gas detection and NFPA 855 separation. 采用磷酸铁锂、UL 9540A测试系统、逸出气体探测及NFPA 855间距。
M | A03: Grid reliability in East Kalimantan (Kalimantan interconnected grid) is lower than JAMALI. A03：东加里曼丹电网（加里曼丹互联电网）可靠性低于JAMALI电网。 | Longer fuel autonomy, generator run-hours budget and BESS for grid support. 延长燃油自持、预留发电机运行小时并配置储能支撑电网。
M | A03: Long-lead equipment (transformers, generators, MV switchgear) currently 12–24 months. A03：长周期设备（变压器、发电机、中压开关柜）交期12–24个月。 | Early procurement / reservation agreements and framework contracts. 提前采购/产能预留及框架合同。
M | A06: HV connection > 30 MVA needs a dedicated 150 kV substation and 18–36 months of PLN works. A06：超过30 MVA的高压接入需专用150 kV变电站及18–36个月电网工程。 | Start the PLN application (SLO, PJBTL) at feasibility; consider phased energisation. 可研阶段即启动PLN申请（SLO、供电协议）；考虑分期送电。
M | A08: Synchronous GPU load swings (tens of % within seconds) stress UPS, generators and the PLN grid. A08：GPU同步负荷波动（数秒内数十个百分点）冲击UPS、发电机及PLN电网。 | BESS included for smoothing; confirm ramp-rate limits with PLN. 已配置储能平抑；与PLN确认爬坡率限值。

## Slide 64: Eleven Indonesian benchmark designs at a glance
11个印尼基准设计一览
Design 设计 | MW | Tier | Cooling 制冷 | PUE | CAPEX | M/MW | RFS | IRR / TCO
A01 Edge micro data center — 250 kW 边缘微型数据中心——250 kW | 0.25 | II | Air-cooled chillers + CRAH / fan wall | 1.51 | USD 4 M | 11.9 | 18 mo | 5.9 %
A02 Enterprise data center — 1 MW 企业数据中心——1 MW | 1 | III | Air-cooled chillers + CRAH / fan wall | 1.51 | USD 18 M | 12.0 | 21 mo | TCO 281/kW·mo
A03 Government / sovereign data center — 5 MW 政府/主权数据中心——5 MW | 5 | IV | Air-cooled chillers + CRAH / fan wall | 1.51 | USD 89 M | 15.3 | 28 mo | TCO 293/kW·mo
A04 Modular prefabricated data center — 2 MW 模块化预制数据中心——2 MW | 2 | III | Air-cooled chillers + CRAH / fan wall | 1.50 | USD 32 M | 13.6 | 21 mo | TCO 292/kW·mo
A05 Retail colocation — 10 MW 零售型托管——10 MW | 10 | III | Water-cooled chillers + cooling towers + CRAH / fan wall | 1.39 | USD 132 M | 11.0 | 28 mo | 8.0 %
A06 Wholesale / build-to-suit — 30 MW 批发型/定制建设——30 MW | 30 | III | Direct liquid cooling | 1.28 | USD 405 M | 11.3 | 40 mo | 7.4 %
A07 Hyperscale cloud campus — 100 MW 超大规模云园区——100 MW | 100 | III | Direct liquid cooling | 1.28 | USD 1,208 M | 10.2 | 40 mo | 7.0 %
A08 AI factory — 50 MW liquid-cooled AI算力中心——50 MW液冷 | 50 | III | Direct liquid cooling | 1.19 | USD 657 M | 11.1 | 40 mo | 11.0 %
A09 Highland high-efficiency DC — 20 MW 高原高能效数据中心——20 MW | 20 | III | Direct liquid cooling | 1.23 | USD 266 M | 11.3 | 28 mo | 6.8 %
A10 AI gigawatt-class campus — 600 MW AI吉瓦级园区——600 MW | 600 | III | Direct liquid cooling | 1.18 | USD 7,256 M | 10.2 | 54 mo | 11.5 %
A11 Regional edge data center — 25 MW 区域边缘数据中心——25 MW | 25 | III | Water-cooled chillers + cooling towers + CRAH / fan wall | 1.38 | USD 339 M | 11.4 | 36 mo | 9.6 %

## Slide 65: What real projects show (1/3): parameters by facility type
真实项目结论（1/3）：按设施类型的技术参数
Facility type 设施类型 | Projects | IT MW | kW / rack | PUE | Tier | Cooling 制冷 | Examples 示例
Enterprise (Owner-operated) 企业自建（自用） | 2 | – | – | – | IV | Chilled water 冷冻水 | Bank Indonesia · Bank Central Asia
Retail Colocation 零售型托管 | 4 | 23–200 | 5–15 | 1.24 | III / IV | Chilled water 冷冻水 | DCI Indonesia · NTT · Digital Edge · EdgeConneX
Wholesale / Build-to-Suit 批发型 / 定制建设 | 1 | 72 | – | – | – | – – | DayOne
Hyperscale / Cloud 超大规模 / 云 | 10 | 54–500 | 40–100 | 1.07–1.15 | III | Direct-to-chip liquid, Evaporative, Seawater, Air 冷板液冷、蒸发、海水、风冷 | Princeton Digital Group · Digital Edge · NeutraDC Nxera Batam · Microsoft Azure
AI Factory / HPC AI算力中心 / 高性能计算 | 8 | 150–5,000 | 100–500 | 1.30 | III | Direct-to-chip liquid 冷板液冷 | BDx · YTL AI Data Centre · Microsoft · Stargate
Edge / Micro Data Center 边缘 / 微型数据中心 | 1 | 6.0 | 3.2 | – | II | Air 风冷 | Telkom neuCentrIX
Government / Sovereign 政府 / 主权数据中心 | 1 | 80 | – | – | IV | – – | Pusat Data Nasional
Modular / Prefabricated 模块化 / 预制式 | 2 | 1.5 | 3.8 | – | III | Air 风冷 | Space DC · Huawei prefabricated modular data center
Publicly reported values (operators, trade press, datasheets); kW/rack marked ≈ is IT ÷ racks. Each project and its sources are in the website reference library. 公开报道数值（运营商、行业媒体、数据表）；“≈”机柜功率为IT÷机柜数。各项目及来源见网站参考项目库。

## Slide 66: What real projects show (2/3): findings by facility type
真实项目结论（2/3）：各类型要点
Enterprise (Owner-operated)
企业自建（自用）
Enterprise (bank) data centers are owner-operated and multi-site — BCA runs primary and secondary sites in Jakarta, Surabaya and Cibitung certified on operations (ISO 9001, ISO/IEC 27001, ISO/IEC 20000-1); central-bank infrastructure goes to Tier IV (Bank Indonesia, reported 2025). Typical 0.5–5 MW, 5–10 kW/rack, chilled water, Tier III–IV, with a disaster-recovery site.
企业（银行）数据中心由业主自营并多站点部署——BCA在雅加达、泗水及芝比通设主备站点，运营获ISO 9001、ISO/IEC 27001及ISO/IEC 20000-1认证；央行基础设施达到Tier IV（印尼央行，2025年报道）。典型0.5–5 MW、5–10 kW/柜、冷冻水、Tier III–IV，并设灾备站点。
Retail Colocation
零售型托管
Jakarta colocation campuses are 23–200 MW: EDGE2 has 23 MW for 3,400+ racks (≈ 6.8 kW/rack average) at an annualised PUE of 1.24; NTT JKT3 45 MW at 5–15 kW/rack with a chilled-water cooling wall; DCI Cibitung 73 MW with Uptime Tier IV. New halls are liquid-cooling-ready for AI tenants (DCI JK6, EDGE2).
雅加达托管园区规模为23–200 MW：EDGE2以23 MW承载3,400余个机柜（平均约6.8 kW/柜），年均PUE 1.24；NTT JKT3为45 MW、5–15 kW/柜，采用冷冻水冷却墙；DCI芝比通73 MW并获Uptime Tier IV。新机房均为AI租户预留液冷（DCI JK6、EDGE2）。
Wholesale / Build-to-Suit
批发型 / 定制建设
Wholesale / build-to-suit campuses of 50–120 MW secure PLN capacity well above the IT load: DayOne Batam 72 MW with a 511 MVA PLN agreement; NeutraDC Nxera Batam 54 MW with up to 90 MVA, Tier III design and liquid cooling at 40–100 kW/rack.
批发/定制园区规模为50–120 MW，PLN容量远高于IT负载：DayOne巴淡72 MW，PLN协议511 MVA；NeutraDC Nxera巴淡54 MW，最高90 MVA，Tier III设计，液冷40–100 kW/柜。
Hyperscale / Cloud
超大规模 / 云
Hyperscale campuses are 100–200 MW and more: PDG JC3 120 MW with dual PLN feeds and direct-to-chip cooling (USD 1 bn ≈ USD 8.3 M/MW); AirTrunk JHB1 150 MW at a design PUE of 1.15 with liquid + indirect evaporative cooling; cloud regions in Jakarta (AWS, Microsoft, Google) are built as three availability zones.
超大规模园区达100–200 MW以上：PDG JC3 120 MW，PLN双进线、冷板液冷（10亿美元≈830万美元/MW）；AirTrunk JHB1 150 MW，设计PUE 1.15，液冷+间接蒸发冷却；雅加达云区域（AWS、微软、谷歌）均按3个可用区建设。

## Slide 67: What real projects show (3/3): findings by facility type
真实项目结论（3/3）：各类型要点
AI Factory / HPC
AI算力中心 / 高性能计算
AI factories are planned at hundreds of MW to GW (BDx CGK4 500 MW with 845 MVA; YTL Kulai 600 MW park; Stargate Abilene 1.2 GW). Racks are GB200 / GB300 NVL72-class at 120–142 kW with closed-loop direct-to-chip cooling (Abilene: air-cooled heat exchangers, zero evaporation; Fairwater: > 90 % liquid); next generations reach 500 kW/rack (BDx). Batteries buffer GPU swings (xAI Colossus).
AI算力中心规划规模为数百MW至GW级（BDx CGK4 500 MW、845 MVA；YTL Kulai园区600 MW；Stargate Abilene 1.2 GW）。机柜为GB200/GB300 NVL72级120–142 kW，采用闭式冷板液冷（Abilene：风冷换热器、零蒸发；Fairwater：>90%液冷）；下一代可达500 kW/柜（BDx）。电池缓冲GPU负荷波动（xAI Colossus）。
Edge / Micro Data Center
边缘 / 微型数据中心
Edge in Indonesia means many small rooms close to users: Telkom neuCentrIX runs ≈ 1,900 racks over 18–20 cities for ≈ 6 MW in total (≈ 3 kW per rack on average; e.g. 29 racks, Tier II, at Ulin Banjarmasin). Plan 0.1–1 MW per site, 3–8 kW/rack, Tier II–III, DX or in-row cooling and remote operation.
印尼的边缘数据中心是大量靠近用户的小型机房：Telkom neuCentrIX在18–20个城市共约1,900个机柜、合计约6 MW（平均每柜约3 kW；如马辰乌林站点29柜、Tier II）。单站规划0.1–1 MW、3–8 kW/柜、Tier II–III、直膨或列间空调并远程运维。
Government / Sovereign
政府 / 主权数据中心
Government / sovereign: PDN Cikarang is Tier IV, 20 MW expandable to 80 MW, with ≈ 25,000 cores and 40 PB of storage; government data should be hosted at SNI 8799 Strata III / Tier III or above.
政府/主权：PDN芝加朗为Tier IV，20 MW可扩至80 MW，约25,000个计算核心及40 PB存储；政府数据应托管于SNI 8799 Strata III/Tier III及以上设施。
Modular / Prefabricated
模块化 / 预制式
Prefabricated / containerised builds trade flexibility for speed: Space DC JAK2 delivered 1.45 MW at 3.8 kW/rack with Uptime Tier III, and Huawei modules for 3 Indonesia were installed in 40 days instead of ≈ 3 months. Use 0.25–5 MW blocks at 4–15 kW/rack unless AI pods are added.
预制/集装箱式建设以灵活性换取速度：Space DC JAK2以3.8 kW/柜交付1.45 MW并获Uptime Tier III；华为为3 Indonesia提供的模块40天完成安装（原约3个月）。除非加装AI舱，宜采用0.25–5 MW单元、4–15 kW/柜。

## Slide 68: Linked parameters in the simulation (1/2): power
模拟中的联动参数（1/2）：供电
System 系统 | When you change 修改 | These follow automatically 自动联动 | Rule / code basis 规则/规范依据
Utility & MV 市电与中压 | IT load, design-day PUE, Tier IT负载、设计日PUE、等级 | PLN voltage class, number of feeds, MV switchgear type (AIS / GIS), 150/20 kV transformers PLN电压等级、进线数、中压开关类型（AIS/GIS）、150/20 kV主变 | ≤ 30 MVA → 20 kV TM, > 30 MVA → 150 kV TT; Tier III+ two feeds; IEC 62271-200 / -203 ≤30 MVA→20 kV中压，>30 MVA→150 kV高压；Tier III及以上两路进线；IEC 62271-200/-203
Transformers 变压器 | Maximum demand, loading limit, Tier 最大需量、负载率上限、等级 | Transformer rating, impedance, quantity, LV ACB frame, switchboard fault rating 变压器容量、阻抗、台数、低压框架断路器、配电柜短路额定 | IEC 60076-1/-5/-11 ratings & uk; IEC 60947-2; IEC 61439-2; one-unit-out loading ≤ 100 % IEC 60076-1/-5/-11容量及阻抗；IEC 60947-2；IEC 61439-2；一台退出后负载率≤100%
Tariff 电价 | IT load and overheads (connection size) IT负载及附加负荷（接入规模） | PLN tariff class PLN电价类别 | B-3/I-3 TM ≈ Rp1,207.6/kWh blended; I-4 TT Rp996.74/kWh (Q4 2026) B-3/I-3中压加权约1,207.6印尼盾/kWh；I-4高压996.74印尼盾/kWh（2026年第四季度）
Generators & fuel 发电机与燃油 | Maximum demand, Tier, PLN grid reliability 最大需量、等级、PLN电网可靠性 | Fuel autonomy, tank size and count, generator rating and quantity 燃油自持时间、储罐规格及数量、发电机容量及台数 | Uptime ≥ 12 h, TIA-942 72 / 96 h; +24 / +48 h weak grids; ≥ 2 tanks Tier III+ (NFPA 110); continuous rating ISO 8528 Uptime≥12 h，TIA-942 72/96 h；弱电网+24/+48 h；Tier III及以上≥2个储罐（NFPA 110）；持续功率ISO 8528
UPS & batteries UPS与电池 | Battery chemistry, Tier, facility type 电池类型、等级、设施类型 | Autonomy (min), room criteria 后备时间（min）、电池室要求 | LFP 5 min (T-IV 10), VRLA 10 min (T-IV 15); IEEE 485 ageing 1.25; NFPA 855 / UL 9540A or IEC 62485-2 磷酸铁锂5 min（Tier IV 10），铅酸10 min（Tier IV 15）；IEEE 485老化系数1.25；NFPA 855/UL 9540A或IEC 62485-2
Busway & rack power 母线与机柜供电 | Racks per row, rack density 每排机柜数、机柜功率 | Row load, busway rating, rack tap-off 每排负载、母线额定、机柜插接箱 | 2N A + B, each carries the row; IEC 61439-6; IEC 60309 tap-offs 2N A+B，各自承担整排；IEC 61439-6；IEC 60309插接
BESS 储能 | Purpose (GPU buffer / weak grid / peak shaving) 用途（GPU缓冲/弱电网/削峰） | Power share of IT, duration, containers 功率占IT比例、时长、集装箱数 | 15 % × 1 h (AI), 10 % × 2 h (grid / peak); 5 MWh containers; NFPA 855 separation 15%×1 h（AI），10%×2 h（电网/削峰）；5 MWh集装箱；NFPA 855间距
AUTO values follow the rule when a source changes; editing one makes it MANUAL and ↺ restores the rule. 自动值随来源参数变化；修改后转为手动，↺恢复规则值。

## Slide 69: Linked parameters in the simulation (2/2): cooling, fire & monitoring
模拟中的联动参数（2/2）：制冷、消防与监控
System 系统 | When you change 修改 | These follow automatically 自动联动 | Rule / code basis 规则/规范依据
Air cooling 风冷 | Air-cooled racks, rack load, ΔT, Tier 风冷机柜数、单柜负载、温差、等级 | Hall heat, airflow, fan walls incl. redundancy 机房热负荷、风量、风墙（含冗余） | ASHRAE TC 9.9 supply 18–27 °C; N+20 % terminals ASHRAE TC 9.9送风18–27 °C；末端N+20%
Chilled water 冷冻水 | Chilled-water load, Tier 冷冻水负荷、等级 | Chiller frame size, quantity, flow, header DN, tower heat 冷机机型、台数、流量、主干管管径、冷却塔散热量 | AHRI 550/590 frames 1,407 / 2,461 / 3,517 kW (water-cooled); ≤ 2.4 m/s headers AHRI 550/590机型1,407/2,461/3,517 kW（水冷）；主干管≤2.4 m/s
Thermal storage 蓄冷 | Tier 等级 | Ride-through time and tank volume 后备时间及储罐容积 | 5 / 10 / 15 min (below T-III / T-III / T-IV continuous cooling) 5/10/15 min（Tier III以下/III/IV连续制冷）
Liquid cooling 液冷 | Heat to liquid 液冷热量 | CDU frame, standby CDUs, dry coolers CDU机型、备用CDU、干冷器 | ≈ 800 kW below 3 MW, ≈ 1,500 kW above; 1 standby per 4 duty 3 MW以下约800 kW，以上约1,500 kW；每4台工作配1台备用
Gas suppression 气体灭火 | Room area & height, agent, hazard class 房间面积及高度、灭火剂、火灾类别 | Protected volume, design concentration, agent mass, NOAEL check 保护容积、设计浓度、灭火剂用量、NOAEL校核 | NFPA 2001 / ISO 14520: × 1.2 Class A, × 1.35 Class C; NOAEL 9 % / 10 % NFPA 2001/ISO 14520：A类×1.2，C类×1.35；NOAEL 9%/10%
CCTV 视频监控 | Resolution, codec, cameras, retention 分辨率、编码、摄像机数、保存天数 | Bit rate, storage (TB), network load 码率、存储容量（TB）、网络负载 | IEC 62676-4 planning; 90-day retention practice IEC 62676-4规划；90天保存惯例
Monitoring 监控系统 | IT load IT负载 | Transformers, UPS, busway runs → BMS points & EPMS meters 变压器、UPS、母线数→BMS点位及EPMS电表 | Scaled from the design basis topology 按设计基准拓扑等比例换算
AUTO values follow the rule when a source changes; editing one makes it MANUAL and ↺ restores the rule. 自动值随来源参数变化；修改后转为手动，↺恢复规则值。

## Slide 70: From knowledge to decision: simulation and assessment
从知识到决策：技术模拟与项目评估
Project Technology Simulation
项目技术模拟
Five interactive one-slide systems: whole facility, critical power, chilled-water cooling, direct liquid cooling, fire · security · monitoring.
五个交互式单页系统：整体设施、关键供电、冷冻水风冷、冷板液冷、消防·安防·监控。
Every equipment hotspot opens a panel with an illustration, how it works, linked calculator, specification & TPG extract and standards.
每个设备热点打开面板：示意图、工作原理、联动计算器、技术规范及TPG摘录与标准。
Choose a benchmark or your own project as the design basis.
可选择基准设计或自己的项目作为设计基准。
Project Assessment
项目评估
Enter location, type and IT load; 47 parameters are proposed with their basis and can be overridden.
输入地点、类型及IT负载；47项参数自动提出并附依据，均可修改。
5 input steps, 13 result pages, reference library with 11 benchmark designs (view or use as template) and 22 real projects.
5个输入步骤、13个结果页面、参考项目库（11个基准设计可查看或用作模板，22个真实项目）。
Proposal report export: Word, Excel, PDF.
项目建议书导出：Word、Excel、PDF。
One knowledge base feeds the deck, the Technical Specification & TPG, the simulation and the assessment: https://alexandervsq.github.io/Data-Center-Project-Assessment/
同一知识库同时驱动本演示文稿、技术规范及TPG、技术模拟与项目评估。

## Slide 71
Key takeaways
要点总结
Size a data center by IT load (MW) and rack density; everything else follows.
以IT负载（MW）和机柜密度确定规模，其他一切随之而定。
Choose the Tier from business risk — it drives redundancy, space and ≈ ±30% CAPEX.
根据业务风险选择Tier——它决定冗余、空间及约±30%的投资。
Power and cooling chains must have no single point of failure for Tier III+.
Tier III及以上的供电与制冷链不得存在单点故障。
AI densities (40–140 kW/rack) require liquid cooling and heavier, taller buildings.
AI密度（40–140 kW/柜）需要液冷及更高承载、更高净高的建筑。
Grid capacity, long-lead equipment and permits usually set the schedule.
电网容量、长周期设备和许可通常决定进度。
Energy is ≈ 70 % of OPEX: PUE, tariff class and returns must be tested together.
电费约占运营成本70%：须同时检验PUE、电价类别与回报。
Companion resources: Technical Specification & TPG (Word) · website with Project Technology Simulation and Project Assessment
配套资料：技术规范书及技术参数保证表（Word）· 含项目技术模拟与项目评估的网站